APPENDIX A

A.1 R410A heat pump modeling approach

This section describes the R410A modelling approach used to simulate the dynamic behavior of the baseline cycle, similar to the one described in section 2.2. Figure A.1 presents the Modelica model schematics of the R410A heat pump. The real system used a 4-way valve to reverse the operating mode, heating and cooling modes were split as it simplifies the model without affecting the final results. Table A.1 provides the characteristics and physical parameters of the main components.

| (a) | (b) |
| --- | --- |

Figure A.1. Schematics of the R410A heat pump in (a) heating mode (b) cooling mode as implemented in Dymola.

Table A.1. Component parameters of the R410A heat pump.

| Component name | R410A cycle |
| --- | --- |
| Compressor | Type: scroll semi-hermetic Displacement: 88.4 cm3 |
| Indoor heat exchanger | Type: plate Material: steel Heat transfer area: 1.48 m2 Size: 300 mm, 10 mm Number of plates: 38 |
| Outdoor heat exchanger | Fin-tube Material: copper/aluminum Heat transfer area: 74.8 m2 Outer tube diameter: 15.875mm Size: 1250 mm, 750 mm, 15 mm |
| Expansion Valve | 480 steps |
| Receiver/accumulator | 4 l |

### A.1.1 Scroll compressor

The scroll compressor was modeled as a black box component. Its three principal outputs—mass flow rate, discharge temperature, and power consumption—were determined using polynomial correlations. The coefficients for these correlations, provided by the manufacturer [1], depended on condenser or evaporator temperature and compressor speed, as shown in Eq. A.1 and Table A.2 The manufacturer specifies the coefficients for these polynomials.

| mref, Td,Wcom =fTev,Tc,Ncom | (A.1) |
| --- | --- |

Table A.2. Coefficients for the scroll compressor correlations A.1

| N (Hz) | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | C9 | C10 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Discharge temperature |  |  |  |  |  |  |  |  |  |  |
| 25 | 7.602084 | -1.133017 | 1.969090 | -0.008548 | 0.034784 | -0.020422 | -0.000593 | 0.000967 | -0.000867 | 0.000314 |
| 30 | 6.773720 | -1.111801 | 2.051333 | -0.006753 | 0.035578 | -0.022460 | -0.000668 | 0.000870 | -0.000825 | 0.000316 |
| 35 | 7.018986 | -1.113057 | 2.055501 | -0.005424 | 0.035935 | -0.021919 | -0.000660 | 0.000775 | -0.000794 | 0.000299 |
| 40 | 9.734082 | -1.025395 | 1.910958 | -0.004938 | 0.031919 | -0.018387 | -0.000658 | 0.000723 | -0.000725 | 0.000263 |
| 45 | 13.304532 | -0.926958 | 1.707297 | -0.004942 | 0.027146 | -0.013582 | -0.000660 | 0.000696 | -0.000652 | 0.000218 |
| 50 | 16.693847 | -0.824204 | 1.517850 | -0.004990 | 0.022107 | -0.009191 | -0.000677 | 0.000682 | -0.000578 | 0.000177 |
| 55 | 19.642006 | -0.759641 | 1.358410 | -0.005347 | 0.018512 | -0.005506 | -0.000676 | 0.000678 | -0.000525 | 0.000142 |
| 60 | 22.315050 | -0.710305 | 1.216845 | -0.005801 | 0.015421 | -0.002248 | -0.000671 | 0.000682 | -0.000479 | 0.000111 |
| 65 | 24.708871 | -0.677125 | 1.093172 | -0.006279 | 0.012843 | 0.000587 | -0.000658 | 0.000690 | -0.000442 | 0.000084 |
| 70 | 26.824192 | -0.660452 | 0.986907 | -0.006666 | 0.010733 | 0.003022 | -0.000633 | 0.000698 | -0.000411 | 0.000061 |
| Mass flow rate |  |  |  |  |  |  |  |  |  |  |
| 25 | 0.059067 | 0.002046 | 0.000176 | 0.000028 | 0.000004 | -0.000005 | 0.000000204 | -0.000000022 | -0.000000096 | 0.000000004 |
| 30 | 0.071126 | 0.002503 | 0.000252 | 0.000035 | 0.000002 | -0.000007 | 0.000000248 | -0.000000042 | -0.000000066 | 0.000000036 |
| 35 | 0.083703 | 0.002941 | 0.000258 | 0.000041 | 0.000001 | -0.000008 | 0.000000294 | -0.000000044 | -0.000000052 | 0.000000041 |
| 40 | 0.096159 | 0.003375 | 0.000270 | 0.000047 | 0.000001 | -0.000008 | 0.000000340 | -0.000000045 | -0.000000042 | 0.000000046 |
| 45 | 0.108495 | 0.003805 | 0.000290 | 0.000053 | 0.0000003 | -0.000009 | 0.000000384 | -0.000000045 | -0.000000035 | 0.000000052 |
| 50 | 0.120396 | 0.004213 | 0.000345 | 0.000059 | 0.000001 | -0.000011 | 0.000000428 | -0.000000037 | -0.000000046 | 0.000000067 |
| 55 | 0.132454 | 0.004633 | 0.000382 | 0.000065 | 0.000001 | -0.000012 | 0.000000471 | -0.000000035 | -0.000000048 | 0.000000076 |
| 60 | 0.144394 | 0.005050 | 0.000424 | 0.000071 | 0.000002 | -0.000013 | 0.000000513 | -0.000000032 | -0.000000054 | 0.000000085 |
| 65 | 0.156215 | 0.005464 | 0.000474 | 0.000076 | 0.000003 | -0.000014 | 0.000000555 | -0.000000028 | -0.000000063 | 0.000000095 |
| 70 | 0.167918 | 0.005873 | 0.000530 | 0.000082 | 0.000004 | -0.000016 | 0.000000596 | -0.000000023 | -0.000000076 | 0.000000105 |
| 75 | 0.179503 | 0.006279 | 0.000592 | 0.000087 | 0.000005 | -0.000017 | 0.000000636 | -0.000000017 | -0.000000092 | 0.000000116 |
| 80 | 0.190969 | 0.006682 | 0.000661 | 0.000093 | 0.000006 | -0.000019 | 0.000000676 | -0.000000010 | -0.000000112 | 0.000000128 |
| 85 | 0.202316 | 0.007080 | 0.000737 | 0.000098 | 0.000008 | -0.000021 | 0.000000714 | -0.000000002 | -0.000000135 | 0.000000140 |
| 90 | 0.213546 | 0.007475 | 0.000819 | 0.000104 | 0.000010 | -0.000023 | 0.000000752 | 0.000000006 | -0.000000162 | 0.000000153 |
| 95 | 0.228556 | 0.007856 | 0.000433 | 0.000110 | 0.000015 | -0.000008 | 0.000000783 | -0.000000036 | -0.000000253 | -0.000000003 |
| 100 | 0.239741 | 0.008243 | 0.000505 | 0.000115 | 0.000018 | -0.000010 | 0.000000819 | -0.000000029 | -0.00000029 | 0.000000003 |
| Compressor power |  |  |  |  |  |  |  |  |  |  |
| 25 | 140.952 | -60.026 | 74.980 | -1.273 | 1.559 | -0.747 | -0.009344 | 0.013251 | -0.010682 | 0.013752 |
| 30 | 217.872 | -73.113 | 86.387 | -1.566 | 1.944 | -0.793 | -0.011760 | 0.018199 | -0.013215 | 0.014326 |
| 35 | 314.537 | -85.475 | 98.091 | -1.854 | 2.331 | -0.851 | -0.014134 | 0.023103 | -0.015922 | 0.014999 |
| 40 | 430.950 | -97.112 | 110.092 | -2.136 | 2.719 | -0.921 | -0.016466 | 0.027965 | -0.018803 | 0.015771 |
| 45 | 567.110 | -108.023 | 122.391 | -2.413 | 3.108 | -1.004 | -0.018756 | 0.032783 | -0.021860 | 0.016644 |
| 50 | 723.016 | -118.209 | 134.987 | -2.685 | 3.498 | -1.099 | -0.021005 | 0.037558 | -0.025091 | 0.017616 |
| 55 | 898.669 | -127.670 | 147.880 | -2.951 | 3.889 | -1.207 | -0.023211 | 0.042290 | -0.028498 | 0.018689 |
| 60 | 1094.069 | -136.406 | 161.071 | -3.211 | 4.281 | -1.327 | -0.025376 | 0.046978 | -0.032079 | 0.019861 |
| 65 | 1309.215 | -144.416 | 174.559 | -3.466 | 4.674 | -1.460 | -0.027498 | 0.051624 | -0.035835 | 0.021134 |
| 70 | 1544.109 | -151.701 | 188.344 | -3.716 | 5.068 | -1.605 | -0.029579 | 0.056226 | -0.039765 | 0.022506 |
| 75 | 1798.749 | -158.260 | 202.426 | -3.960 | 5.464 | -1.763 | -0.031618 | 0.060785 | -0.043871 | 0.023978 |
| 80 | 2073.136 | -164.094 | 216.806 | -4.199 | 5.860 | -1.933 | -0.033615 | 0.065300 | -0.048151 | 0.025550 |
| 85 | 2367.270 | -169.203 | 231.484 | -4.432 | 6.257 | -2.115 | -0.035570 | 0.069773 | -0.052606 | 0.027222 |
| 90 | 2681.150 | -173.587 | 246.458 | -4.660 | 6.656 | -2.310 | -0.037484 | 0.074202 | -0.057236 | 0.028994 |
| 95 | 3014.777 | -177.245 | 261.730 | -4.882 | 7.056 | -2.517 | -0.039355 | 0.078588 | -0.062041 | 0.030866 |
| 100 | 3368.151 | -180.178 | 277.299 | -5.099 | 7.456 | -2.736 | -0.041185 | 0.082930 | -0.067020 | 0.032838 |

### A.1.2 Condenser/evaporator

The condenser and evaporator alternated between operating modes. In cooling mode, the outdoor heat exchanger (OHX) served as an evaporator. The indoor heat exchanger worked as a condenser. Table A.3 shows the main heat exchanger characteristics, secondary fluids, and system arrangement. In heating mode, these roles were reversed. To address non-linear variations in fluid properties, the heat exchangers were divided into control volumes. This followed the TIL suite package methodology. The indoor heat exchanger (IHX) was modeled with the TIL.HeatExchangers.Plate.VLEFluidLiquid.ParallelFlowHX component. R410A was used as the vapor-liquid equilibrium (VLE) fluid, and a 70 %/30 % water/ethylene glycol mixture was used as the secondary fluid. Table A.4 summarizes the heat transfer correlations from the TIL suite package [2] for both sides. The OHX was modeled with the TIL.HeatExchangers.FinAndTube.-MoistAirVLEFluidLiquid.ParallelFlowHX component with moist air as the secondary fluid. Further details on the modeling approach are available in [3].

Table A.3. Heat exchanger model characteristics of the R410A heat pump model.

| Refrigerant | Heat exchanger | Mode | Secondary fluid | Arrangement |
| --- | --- | --- | --- | --- |
| R410A | Condenser | Heating | Ethylene-glycol 30% | Counter-current |
|  | Condenser | Cooling | Air | Cross-flow |
|  | Evaporator | Heating | Air | Cross-flow |
|  | Evaporator | Cooling | Ethylene-glycol 30% | Co-current |

Table A.4. Heat transfer correlations for R410A heat exchangers available in Dymola + TIL suite package 2025x [2].

| Working fluid | Heat transfer |
| --- | --- |
| Single phase supercritical | Dittus-Boelter |
| Two phase evaporation | Shah/Chen |
| Single phase (IHX) | Dittus-Boelter/Gnielinski |
| Two phase condensation | Shah |
| Single phase water | Gnielinski |
| Moist air | Haaf |

The rest of components were modelled as described in section 2, using Dymola and components available in TIL package. The electronic expansion valve was modeled as an isenthalpic throttle with similar approach as in section 2.2.3 controlled by a standard PI logic regulating the superheating in the evaporator. The accumulator was modeled using the TIL component.VLEFluid-Components.Separator in TIL Library, with a volume of 4 liters. Auxiliary components, such as pumps and fans to provide the secondary fluid flow rates, were modeled following TIL.LiquidComponents.Pumps.SimplePump and TIL.GasComponents.Fans.SimpleFan in TIL Library, like the approach described in section 2.2.4

APPENDIX B

### B.1 R744 heat pump modeling approach

### B.1.1 R744 reciprocating compressor

The coefficients presented in Table B.1 were obtained from the manufacturer [4].

Table B.1. Coefficients for the reciprocating compressor correlations in Eq.1.

| Frequency (Hz) | C1 | C2 | C3 | C4 |
| --- | --- | --- | --- | --- |
| Volumetric efficiency |  |  |  |  |
| 20 | -0.015373 | 0.181520 | -0.500880 | 1.256729 |
| 30 | -0.005692 | 0.062804 | -0.315758 | 1.311527 |
| 40 | -0.002343 | 0.040733 | -0.274834 | 1.298481 |
| 50 | -0.005763 | 0.068122 | -0.344341 | 1.348485 |
| 60 | -0.016545 | 0.174928 | -0.679059 | 1.664619 |
| Isentropic efficiency |  |  |  |  |
| 20 | -0.020238 | 0.197671 | -0.509725 | 1.040497 |
| 30 | -0.001047 | 0.004029 | -0.039762 | 0.781483 |
| 40 | 0.008700 | -0.076311 | 0.169762 | 0.626423 |
| 52 | 0.003435 | -0.030765 | 0.042698 | 0.730017 |
| 60 | -0.009420 | 0.091973 | -0.328854 | 1.065771 |

References

[1]	Danfoss, A. S. "Coolselector®2." Danfoss A/S. https://www.danfoss.com/en-us/service-and-support/downloads/dcs/coolselector-2/ (accessed January 2026).

[2]	GmbH, TLK-Thermo. "TIL-model library for components of thermal system." https://www.tlk-thermo.com/en/software/til-suite (accessed May 25, 2026).

[3]	Hu, Bin, Li, Yaoyu, Cao, Feng, and Xing, Ziwen, "Extremum seeking control of COP optimization for air-source transcritical CO2 heat pump water heater system," Applied Energy, vol. 147, pp. 361-372, 6 2015, doi: 10.1016/j.apenergy.2015.03.010.

[4]	Bock Gmb, H. "VAP for Stationary Applications." Bock GmbH. https://vap.bock.de/stationaryapplication/Pages/Index.aspx (accessed January 2026).