TABLE 1

Maximum Values for the Metallic Shielding for the Most Commercially Available Cables

| Cross-sectional area (mm²) | Elapsed time to clear the fault (s) | Maximum value of current (A) |
| --- | --- | --- |
| 6 | 0.5 | 978 |
| 6 | 1.0 | 692 |
| 16 | 0.5 | 2609 |
| 16 | 1.0 | 1845 |
| 25 | 0.5 | 4077 |
| 25 | 1.0 | 2883 |
| 148 | 0.5 | 24000 |
| 210 | 1.0 | 24000 |

TABLE 2

35 kV CAPACITIVE COMPONENT OF THE MOST USUAL CABLES [15]

| Conductor area (mm²) | Insulation material | Conductor diameter (mm) | C (mF/km) | 3Ico (A/km) |
| --- | --- | --- | --- | --- |
| 630 | XLPE | 30.2 | 0.262 | 5.9 |
| 500 | EPR | 26.4 | 0.317 | 7.1 |
| 500 | XLPE | 26.4 | 0.243 | 5.4 |
| 400 | XLPE | 23.4 | 0.222 | 5.0 |
| 300 | XLPE | 20.6 | 0.203 | 4.5 |