
TABLE 1
MAXIMUM VALUES FOR THE METALLIC SHIELDING FOR THE MOST COMMERCIALLY AVAILABLE CABLES
	Cross-sectional area (mm²)
	Elapsed time to clear the fault (s)
	Maximum value of current (A)

	6
	0.5
	978

	6
	1.0
	692

	16
	0.5
	2609

	16
	1.0
	1845

	25
	0.5
	4077

	25
	1.0
	2883

	148
	0.5
	24000

	210
	1.0
	24000





TABLE 2
35 kV CAPACITIVE COMPONENT OF THE MOST USUAL CABLES [15]
	Conductor area
(mm²)
	Insulation
material
	Conductor diameter (mm)
	C (mF/km)
	3Ico (A/km)

	630
	XLPE
	30.2
	0.262
	5.9

	500
	EPR
	26.4
	0.317
	7.1

	500
	XLPE
	26.4
	0.243
	5.4

	400
	XLPE
	23.4
	0.222
	5.0

	300
	XLPE
	20.6
	0.203
	4.5



