## README
HRWHPI — Consolidated Blinded Supplementary Information
Recommended use: submit this single workbook as the manuscript supplementary spreadsheet (e.g., Online Resource 1 / Supplementary Material 1), if the journal portal accepts one consolidated file.
Item | Statement
Scope | This workbook consolidates the final rater-neutral instrument, locked scoring reference, expert-confirmed weights, aggregate content-validation outputs, anonymized paired IRR data, and aggregate Mayo/Riyadh evidence-coverage and sensitivity/scenario results.
Blinding | No author names, affiliations, e-mails, expert identifiers, rater names, signatures, coordinator records, or correspondence are included.
Instrument | 72 frozen indicators: 27 Critical Gates, 26 Mandatory, 17 Performance, 2 Enhancement.
Content validation | Only aggregate dichotomized positive counts (ratings 3/4) are reproduced. Exact 3-versus-4 responses are not reconstructed. No expert-level records are included.
Weighting | Final expert-confirmed locked domain and indicator weights are reproduced without expert-identifiable inputs.
IRR | Paired scores are anonymized as Rater 1 and Rater 2. Stage 7 was a controlled calibration IRR exercise; it is not presented as real-world operational reliability.
Critical-gate kappa | If expected agreement Pe = 1, conventional Cohen kappa is mathematically not estimable; the workbook reports NOT ESTIMABLE and retains exact gate agreement.
Mayo/Riyadh case | Evidence-constrained real-case application. Not Evidenced does not mean Non-Compliant. No missing performance score is imputed, and no complete-project HRWHPI is released.
CAL-SIM boundary | Controlled calibration simulation material is not used as evidence of actual Mayo/Riyadh performance.
Journal guideline | https://link.springer.com/journal/43995/submission-guidelines
Source control (file-level SHA-256; source files retained separately in the study audit archive)
Source component | SHA-256
Final rater-neutral V1.2 instrument | 978679f9b7d44f6e0d3efddea5733039cd80753a69bc714776cc265d4d23ffab
Stage 5 locked weights | fd8639d8be8f00c0caab949d3b6bc00cc7ec40fa12f1e63a346d915abc8a58e7
Delphi R1 content validation | ca772f609e5b20c525c631871ebef1f31d56b4d6f21040c0eaecaa71add5ecc0
Final completed IRR analysis | 9820a64e65d8725c4a3aa0954b4398c6c36b5ed131bf0352bd7d26ad9a935a68
Stage 8D evidence/uncertainty analysis | d9ec405927199dbbb635d6884491f71765606d3f0f3c36b0f1763ed3788f57b3
Stage 8E sensitivity/scenario analysis | 6d62098912a1641b21901d8562f31531ff0be880d4baaa55b6d6f4d8ff00b8bb

## INSTRUMENT_72
HRWHPI Final Rater-Neutral Instrument — 72 Frozen Indicators
Frozen wording is reproduced exactly from the deployed V1.2 instrument. Rater-input fields are intentionally omitted from this consolidated supplement.
Indicator_ID | Domain_ID | Class | Frozen_Wording | Scoring_Archetype | Critical_Gate_Flag
V2-REG-01 | D1 | Critical Gate | يوثق المشروع مسار الترخيص وموافقات الجهة ذات الاختصاص لكل مرحلة، مع حالة كل موافقة والاشتراطات المفتوحة والمانعة. | Regulatory / gate compliance
V2-REG-02 | D1 | Mandatory | يربط كل مؤشر قابل للامتثال بالمرجع الساري وإصدار الكود والبند أو منهج التحقق والجهة صاحبة الاختصاص. | Regulatory / gate compliance
V2-REG-03 | D1 | Mandatory | يوثق كل استثناء أو انحراف تنظيمي بمبرر فني وموافقة مكتوبة من الجهة المخولة قبل اعتباره مقبولًا. | Regulatory / gate compliance
V2-REG-04 | D1 | Mandatory | يميز HRWHPI بوضوح بين التقييم المبدئي قبل الترخيص والامتثال المثبت بعد استلام الوثائق والموافقات الرسمية. | Regulatory / gate compliance
V2-SIT-01 | D1 | Critical Gate | يثبت المشروع مشروعية الاستعمال والارتفاع والارتدادات ووصول الإطفاء والإسعاف قبل احتساب أي درجة أداء كلية. | Regulatory / gate compliance
V2-SIT-02 | D1 | Critical Gate | يفصل التصميم الخارجي بقدر الإمكان بين الإسعاف والإطفاء والخدمات والجمهور، ويختبر نقاط التقاطع المتبقية تحت الذروة والطوارئ. | Process / completeness / readiness
V2-SIT-03 | D1 | Critical Gate | يحدد المشروع تعارضات الموقع وقدرة الكهرباء والمياه والصرف والخدمات الداعمة ويغلق المخاطر المانعة قبل اعتماد الموقع. | Regulatory / gate compliance
V2-SIT-04 | D1 | Performance | يقاس الوصول الصحي الآمن للمشاة في المناخ الحار بزمن ومسافة المشي والتظليل والراحة الحرارية والفصل عن المركبات وسهولة الحوامل وذوي الإعاقة. | Quantitative performance
V2-SIT-05 | D1 | Performance | يقاس أداء المواقف والإنزال بزمن الوصول والبحث والانتظار وطول الطابور وأولوية الحوامل وذوي الإعاقة والفصل عن الإسعاف والخدمات. | Quantitative performance
V2-SPA-01 | D2 | Performance | يثبت المشروع اتجاهًا أو مساحة توسع محمية واحتياطيات بنيوية وخدمية تسمح بالنمو دون الإخلال بالمخارج والنواة والمسارات الحرجة. | Functional / spatial performance
V2-SPA-02 | D2 | Performance | تثبت مرونة الطابق النموذجي بإمكانية تغيير الوظائف أو زيادة العناية دون أعمال إنشائية كبيرة أو تعطيل شامل. | Functional / spatial performance
V2-SPA-03 | D2 | Performance | يقيم تأثير النواة وشبكة الأعمدة وارتفاعات الطوابق ومساحة الروافع والفراغات الفنية على المرونة والكفاءة وقابلية إضافة أو تعديل الأنظمة. | Functional / spatial performance
V2-CLN-01 | D2 | Critical Gate | يقاس زمن الانتقال السريري للمسارات الحرجة مثل LDR–OR–NICU والطوارئ–التصوير/المختبر تحت سيناريوات تشغيل وذروة محددة. | Functional / spatial performance
V2-CLN-02 | D2 | Mandatory | تثبت العلاقات السريرية الحرجة بمصفوفة علاقات ومسافات ومحاكاة حركة وزمن بدل الاكتفاء بوصف «قريب/بعيد». | Functional / spatial performance
V2-CLN-03 | D2 | Critical Gate | يقلل التصميم تقاطع الحركة العامة والسريرية والخدمية ويثبت الفصل والتحكم في نقاط العبور والمصاعد المشتركة. | Functional / spatial performance
V2-CLN-04 | D2 | Mandatory | تقاس الخصوصية وتجربة الأسرة في خدمات النساء والولادة وNICU بخطوط الرؤية وفصل المسارات والتحكم بالدخول وملاءمة وجود الأسرة. | Functional / spatial performance
V2-NIC-01 | D2 | Critical Gate | تثبت بيئات NICU وحديثي الولادة استقرار الظروف البيئية والهدوء والمرونة والتنسيق الخدمي داخل المساحات الحساسة. | Environmental / infection-control performance
V2-VRT-01 | D3 | Mandatory | يحدد عدد وتخصيص المصاعد من نموذج طلب فعلي للأسرة والمرضى والمواد والزوار وفترات الذروة، لا من العدد الإجمالي فقط. | Functional / spatial performance
V2-VRT-02 | D3 | Performance | يقاس أداء النقل الرأسي بأزمنة الانتظار والرحلة والمناولة ومستوى الخدمة لكل فئة حركة حرجة وعادية. | Quantitative performance
V2-VRT-03 | D3 | Critical Gate | تتوفر مرونة N-1 أو بديل تشغيلي مكافئ للنقل الرأسي الحرج وفق تحليل الخطورة، بما يشمل الصيانة المخططة لا الطوارئ فقط. | Resilience / failure-scenario performance
V2-VRT-04 | D3 | Critical Gate | تثبت استمرارية المصاعد ومسارات النقل الحرج أثناء الطوارئ والاختبارات والربط المرحلي مع وجود سعة بديلة وخطة rollback. | Resilience / failure-scenario performance
V2-FIR-01 | D4 | Critical Gate | يثبت التصميم استراتيجية دفاع في المكان وتقسيمًا أفقيًا وإخلاءً مرحليًا مناسبًا لمرضى محدودي الحركة والمواليد. | Regulatory / gate compliance
V2-FIR-02 | D4 | Critical Gate | تثبت مخارج الهروب وسعاتها واستمراريتها وعدم إعاقتها للمرضى والعاملين تحت سيناريوات الإشغال والطوارئ. | Regulatory / gate compliance
V2-FIR-03 | D4 | Critical Gate | تتحقق أنظمة التحكم في الدخان بالقياس تحت الحالات العادية وأوضاع الفشل والطاقة الاحتياطية وفق أساس تصميم واضح. | Resilience / failure-scenario performance
V2-FIR-04 | D4 | Critical Gate | تدار سلامة الحواجز والأبواب والاختراقات طوال التنفيذ والتشغيل بسجل قابل للتتبع وفحص قبل الإغلاق وبعد كل تعديل. | Process / completeness / readiness
V2-FIR-05 | D4 | Critical Gate | تختبر وظائف الإنذار والرش والأبواب والدخان والمصاعد والطاقة والمضخات كمنظومة مترابطة مع التحقق من التوقيت والعودة للوضع الطبيعي. | Resilience / failure-scenario performance
V2-FIR-06 | D4 | Critical Gate | يقاس زمن الإخلاء المرحلي للانتقال إلى حجرة آمنة ثم للمراحل اللاحقة عند الحاجة وفق خصائص مرضى مستشفى النساء والمواليد. | Resilience / failure-scenario performance
V2-MEP-01 | D5 | Critical Gate | تثبت منظومة الطاقة الحرجة التكرار والتحويل الآمن واستمرار الأحمال السريرية الحرجة أثناء فقد المصدر والصيانة. | Resilience / failure-scenario performance
V2-MEP-02 | D5 | Critical Gate | تحافظ أنظمة HVAC للمناطق الحرجة على الضغط والحرارة والرطوبة والترشيح أثناء التشغيل الطبيعي وأوضاع الفشل المحددة. | Resilience / failure-scenario performance
V2-MEP-03 | D5 | Critical Gate | تثبت شبكة الغازات الطبية نقاء وضغط وإنذارات وتكرارًا مناسبًا للمناطق الحرجة وتستمر أثناء الفشل والصيانة المخططة. | Resilience / failure-scenario performance
V2-MEP-04 | D5 | Critical Gate | تثبت أنظمة المياه والصرف الاستقلال/الاحتياط وجودة المياه ومنع الارتداد والاستجابة للتسربات دون تعطيل سريري غير مقبول. | Resilience / failure-scenario performance
V2-RES-01 | D5 | Performance | تقاس اعتمادية الأنظمة الحرجة بالتوافر Availability وزمن الاستعادة وMTTR من بيانات تشغيل فعلية أو اختبارات فشل موحدة. | Quantitative performance
V2-RES-02 | D5 | Critical Gate | تثبت الأنظمة الحرجة قابلية العزل والتكرار واستمرار الخدمة أثناء الفشل والصيانة المخططة وفق تحليل الخطورة. | Resilience / failure-scenario performance
V2-RES-03 | D5 | Mandatory | تختبر سيناريوهات Multi-hazard المركبة التي تجمع أخطارًا مترابطة ذات صلة بالموقع والتشغيل بدل اختبار كل نظام منفردًا فقط. | Process / completeness / readiness
V2-RES-04 | D5 | Critical Gate | ينفذ اختبار سيناريو انقطاع موثق لكل نظام حرج لإثبات الاستمرارية والتحويل والعودة الآمنة، لا مجرد مراجعة وجود معدات احتياطية. | Resilience / failure-scenario performance
V2-ENV-01 | D6 | Critical Gate | يطبق ICRA قبل وأثناء الأعمال المرتبطة بمنشأة عاملة مع حواجز وضغط ومسارات عمال ونفايات ورصد وتنظيف متوافق مع مستوى الخطورة. | Environmental / infection-control performance
V2-ENV-02 | D6 | Mandatory | يفصل تدفق النفايات والبياضات والتنظيف عن الجمهور والمسارات النظيفة مع سعة تخزين مؤقت وظروف بيئية مناسبة. | Environmental / infection-control performance
V2-ENV-03 | D6 | Critical Gate | يقيّم خطر جودة الهواء عند مآخذ الهواء بالنسبة للغبار والعوادم والمولدات والتحميل واتجاهات الرياح ويعالج مصادر التلوث غير المقبولة. | Environmental / infection-control performance
V2-ENV-04 | D6 | Performance | يقيس المشروع تعرض المستخدمين والمداخل والفراغات الخارجية للحرارة والغبار والضوضاء والتلوث ويطبق تخفيفًا قابلًا للتحقق. | Environmental / infection-control performance
V2-ENV-05 | D6 | Performance | تقاس النظافة التشغيلية في المناطق الحرجة ومسارات الدعم بمؤشرات تدقيق وبلاغات واستجابة قابلة للتتبع، لا بوصف عام فقط. | Environmental / infection-control performance
V2-ENV-06 | D6 | Enhancement | تختبر جودة الضوء الطبيعي والوهج والراحة الحرارية وخطوط الرؤية والخصوصية في الفراغات السريرية بدل الاعتماد على مساحة الزجاج وحدها. | Environmental / infection-control performance
V2-CON-01 | D7 | Mandatory | تقاس جاهزية التصميم للتنفيذ بمستوى التنسيق والتعارضات المفتوحة وRFIs وجاهزية shop drawings ومساحات التركيب والصيانة. | Process / completeness / readiness
V2-CON-02 | D7 | Mandatory | يقاس نضج BIM والتنسيق متعدد التخصصات بكثافة التعارضات الحرجة المفتوحة واكتمال النموذج ومسؤوليات التحقق قبل الطرح والتنفيذ. | Process / completeness / readiness
V2-CON-03 | D7 | Critical Gate | تحدد نقاط توقف Hold Points للأعمال المخفية الحرجة قبل إغلاق الأسقف والجدران مع أدلة قبول إلزامية. | Process / completeness / readiness
V2-CON-04 | D7 | Performance | تقاس جودة التنفيذ بنسبة نجاح الفحص والاختبار من أول مرة واتجاه NCR وإعادة العمل في الحزم الحرجة. | Quantitative performance
V2-CON-05 | D7 | Critical Gate | تثبت خطط التنفيذ داخل مستشفى عامل فصل الإنشاء عن المرضى والإسعاف والخدمات واستمرارية التشغيل أثناء الرفع والربط والاختبار. | Resilience / failure-scenario performance
V2-CON-06 | D7 | Mandatory | يكتمل ملف الفحص والاختبار لكل حزمة حرجة قبل القبول، مع ربط النتائج بالعيوب والتصحيح وإعادة الاختبار. | Process / completeness / readiness
V2-COM-01 | D7 | Mandatory | تكتمل أعمال Commissioning للأنظمة الحرجة بقبول قائم على الأداء والاختبار والاتجاهات لا على الشهادات المنفردة فقط. | Process / completeness / readiness
V2-COM-02 | D7 | Critical Gate | تنفذ اختبارات تكامل للواجهات بين الطاقة والحريق والدخان والمصاعد وBMS والأنظمة الحرجة ذات الصلة وفق سيناريوات فشل وعودة للوضع الطبيعي. | Resilience / failure-scenario performance
V2-OPS-01 | D7 | Mandatory | تقاس الجاهزية التشغيلية قبل التسليم باكتمال الأعمال والاختبارات والوثائق والتدريب وقطع الغيار والتصاريح وخطة الانتقال. | Process / completeness / readiness
V2-OPS-02 | D7 | Mandatory | يكتمل ملف تسليم الأصول الرقمي والتشغيلي بما يسمح بالتشغيل والصيانة والتتبع بعد الاستلام. | Process / completeness / readiness
V2-OPS-03 | D8 | Performance | تقاس كثافة الاستخدام والذروة الفعلية للفراغات والمصاعد والخدمات لتحديد الفجوة بين افتراضات التصميم والتشغيل. | Quantitative performance
V2-LIF-01 | D8 | Mandatory | تثبت قابلية صيانة الأنظمة والمعدات من حيث الوصول والعزل ومساحة العمل وزمن الإصلاح دون تعطيل سريري غير مقبول. | Operational / lifecycle performance
V2-LIF-02 | D8 | Mandatory | يثبت لكل معدة كبيرة أو حرجة مسار إدخال واستبدال قابل للتنفيذ بعد التشغيل مع الأبعاد والأحمال ونقاط الرفع ومناطق العزل. | Operational / lifecycle performance
V2-LIF-03 | D8 | Mandatory | تقاس جاهزية قطع الغيار الحرجة بالتوفر ومعدل التغطية وزمن التوريد بما يتوافق مع مخاطر وتعطل كل أصل حرج. | Operational / lifecycle performance
V2-LIF-04 | D8 | Mandatory | تثبت تغطية المهارات الفنية الحرجة في كل وردية مع زمن استجابة وإجراءات طوارئ وأدوات مناسبة للأصول الحرجة. | Operational / lifecycle performance
V2-LIF-05 | D8 | Performance | يقاس زمن الاستجابة والإصلاح للأعطال الحرجة والمتكررة ويستخدم الاتجاه لتحديد ضعف قابلية الصيانة أو الموارد. | Quantitative performance
V2-LIF-06 | D8 | Performance | تثبت قابلية تجديد أو استبدال المكونات أثناء استمرار التشغيل من خلال العزل المرحلي والمسارات والبدائل المؤقتة. | Resilience / failure-scenario performance
V2-LIF-07 | D8 | Performance | تراقب حالة التشطيبات والحواجز ذات الأثر على العدوى والحريق والتشغيل وتغلق العيوب بحسب خطورتها. | Operational / lifecycle performance
V2-LIF-08 | D8 | Mandatory | ينفذ تقييم ما بعد الإشغال للتحقق من الأداء الفعلي للحركة والبيئة والصيانة وتجربة المستخدم مقارنة بافتراضات التصميم. | Operational / lifecycle performance
V2-LIF-09 | D8 | Performance | تسجل فجوات التصميم–التشغيل المكتشفة بعد الإشغال وتغلق بإجراءات تصحيح مع مسؤولية وموعد وإثبات أثر. | Operational / lifecycle performance
V2-LIF-10 | D8 | Performance | تقارن البدائل على تكلفة دورة الحياة بما يشمل CAPEX وOPEX والصيانة والاستبدال ضمن افتراضات موثقة ومخاطر تشغيلية. | Economic / option appraisal
V2-DIG-01 | D9 | Mandatory | تقاس جودة بيانات BMS/CMMS من الاكتمال والصحة والتوقيت وقابلية ربط الأصل والإنذار وأمر العمل بما يسمح باستخدامها في القرار والتحقق. | Operational / lifecycle performance
V2-DIG-02 | D9 | Performance | تقاس جودة إدارة الإنذارات بمعدل الإنذارات الكاذبة والمتكررة وأولوية الإنذار وزمن الاستجابة بعد rationalization. | Quantitative performance
V2-DIG-03 | D9 | Enhancement | تستخدم مؤشرات اتجاه وتدهور قابلة للتحقق للكشف المبكر عن فشل الأنظمة الحرجة وربطها بصيانة تنبؤية. | Operational / lifecycle performance
V2-DIG-04 | D9 | Mandatory | يحدد مستوى نضج BIM واكتمال بيانات النموذج اللازمة للتحقق من المساحات والعلاقات والتعارضات والتسليم التشغيلي. | Operational / lifecycle performance
V2-DIG-05 | D9 | Mandatory | ترتبط القرارات الحسابية أو المحاكاة بمسؤول تصميم محدد ومدخلات ونسخة نموذج ونتائج قابلة لإعادة التحقق، ولا تقبل الأوصاف النصية وحدها. | Operational / lifecycle performance
V2-GOV-01 | D9 | Critical Gate | تطبق بوابات Go/No-Go مرحلية تمنع الانتقال عند فشل متطلب حرج غير قابل للتعويض ولا يسمح المتوسط الكلي بتجاوز الفشل. | Regulatory / gate compliance
V2-GOV-02 | D9 | Mandatory | يخضع كل تغيير بعد تجميد التصميم لتقييم أثر موثق على السلامة والتشغيل والتكلفة والبرنامج والموافقات قبل التنفيذ. | Process / completeness / readiness
V2-GOV-03 | D9 | Mandatory | توثق مقارنة البدائل التصميمية بمعايير وأوزان وافتراضات ومخاطر ونتائج قابلة للتدقيق قبل تثبيت البديل. | Process / completeness / readiness
V2-GOV-04 | D9 | Mandatory | تختلف متطلبات دليل HRWHPI ودرجة نضج الإثبات حسب مرحلة الجدوى والتصميم والتنفيذ والتشغيل وما بعد الإشغال مع عدم مساواة الدليل المبدئي بالدليل النهائي. | Process / completeness / readiness
V2-EVD-01 | D9 | Mandatory | يرتبط كل مؤشر بحزمة دليل قابلة للتدقيق تحدد نوع الدليل ومصدره وتاريخه ومرحلة التقييم ومسؤول التحقق وحالة Not Evidenced منفصلة عن Non-Compliant. | Process / completeness / readiness
QC | Indicator count |  | Critical Gates
Note on A1: Source SHA-256: 978679f9b7d44f6e0d3efddea5733039cd80753a69bc714776cc265d4d23ffab

## SCORING_REFERENCE
HRWHPI Locked Scoring Reference — Verbatim V1.2 Method Content
Blinded reproduction of the locked scoring reference. Rater identity labels are anonymized only; no measurement method, evidence requirement, score band, gate rule, or validation logic is substantively edited.
Indicator_ID | Class | Measurement_Method | Evidence_Required | Archetype | Score 4 - LOCKED | Score 3 - LOCKED | Score 2 - LOCKED | Score 1 - LOCKED | Score 0 - LOCKED | Gate PASS Criterion | Source / Benchmark | Clause / Version / Calibration Record | Calibration Status | Calibration Note
V2-REG-01 | Critical Gate | مراجعة سجل الموافقات حسب المرحلة؛ تصنيف المتطلبات إلى مغلقة/مفتوحة/مانعة وتتبع إغلاقها. | Code/Authority matrix؛ permit basis؛ موافقات رسمية؛ سجل الاستثناءات والملاحظات. | Regulatory / gate compliance | INDICATOR TEST — مراجعة سجل الموافقات حسب المرحلة؛ تصنيف المتطلبات إلى مغلقة/مفتوحة/مانعة وتتبع إغلاقها. 4 = 100% of applicable essential/mandatory requirements for the indicator test are Verified as satisfied; required approvals/acceptances are current; no material, blocking, or unapproved exception remains. | INDICATOR TEST — مراجعة سجل الموافقات حسب المرحلة؛ تصنيف المتطلبات إلى مغلقة/مفتوحة/مانعة وتتبع إغلاقها. 3 = all essential/mandatory requirements are satisfied and >=90% of non-critical checklist/record elements are complete; only minor non-material gaps remain; no acceptance-blocking item. | INDICATOR TEST — مراجعة سجل الموافقات حسب المرحلة؛ تصنيف المتطلبات إلى مغلقة/مفتوحة/مانعة وتتبع إغلاقها. 2 = 70% to <90% of non-critical checklist/record elements are complete OR one material but correctable gap remains; no Verified failure of an essential mandatory requirement. | INDICATOR TEST — مراجعة سجل الموافقات حسب المرحلة؛ تصنيف المتطلبات إلى مغلقة/مفتوحة/مانعة وتتبع إغلاقها. 1 = >0% to <70% of required elements are complete/satisfied OR multiple material gaps/open approvals remain; the compliance/control is substantially deficient. | INDICATOR TEST — مراجعة سجل الموافقات حسب المرحلة؛ تصنيف المتطلبات إلى مغلقة/مفتوحة/مانعة وتتبع إغلاقها. 0 = Verified failure/non-compliance of an essential mandatory requirement, rejected/absent required approval, prohibited condition, or required control is absent. | INDICATOR GATE TEST — مراجعة سجل الموافقات حسب المرحلة؛ تصنيف المتطلبات إلى مغلقة/مفتوحة/مانعة وتتبع إغلاقها. PASS = Verified evidence demonstrates 100% satisfaction of all applicable essential mandatory requirements/approvals in the indicator test, with no blocking item, rejected requirement, or unapproved exception. | Applicable Authority Having Jurisdiction (AHJ), adopted local code/permit basis and approved interpretations; HRWHPI Candidate Indicator Set V2.1 FINAL FROZEN RELEASED. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-REG-02 | Mandatory | تدقيق اكتمال clause-by-clause mapping وصحة إصدار المرجع وتحديد AHJ لكل متطلب. | Code register؛ clause matrix؛ قائمة الإصدارات؛ موافقات/تفسيرات الجهة المختصة. | Regulatory / gate compliance | INDICATOR TEST — تدقيق اكتمال clause-by-clause mapping وصحة إصدار المرجع وتحديد AHJ لكل متطلب. 4 = 100% of applicable essential/mandatory requirements for the indicator test are Verified as satisfied; required approvals/acceptances are current; no material, blocking, or unapproved exception remains. | INDICATOR TEST — تدقيق اكتمال clause-by-clause mapping وصحة إصدار المرجع وتحديد AHJ لكل متطلب. 3 = all essential/mandatory requirements are satisfied and >=90% of non-critical checklist/record elements are complete; only minor non-material gaps remain; no acceptance-blocking item. | INDICATOR TEST — تدقيق اكتمال clause-by-clause mapping وصحة إصدار المرجع وتحديد AHJ لكل متطلب. 2 = 70% to <90% of non-critical checklist/record elements are complete OR one material but correctable gap remains; no Verified failure of an essential mandatory requirement. | INDICATOR TEST — تدقيق اكتمال clause-by-clause mapping وصحة إصدار المرجع وتحديد AHJ لكل متطلب. 1 = >0% to <70% of required elements are complete/satisfied OR multiple material gaps/open approvals remain; the compliance/control is substantially deficient. | INDICATOR TEST — تدقيق اكتمال clause-by-clause mapping وصحة إصدار المرجع وتحديد AHJ لكل متطلب. 0 = Verified failure/non-compliance of an essential mandatory requirement, rejected/absent required approval, prohibited condition, or required control is absent. | N/A - non-critical indicator | Applicable Authority Having Jurisdiction (AHJ), adopted local code/permit basis and approved interpretations; HRWHPI Candidate Indicator Set V2.1 FINAL FROZEN RELEASED. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-REG-03 | Mandatory | نسبة الاستثناءات ذات ملف مكتمل وموافقة مكتوبة؛ تتبع الاستثناءات المفتوحة والمانعة. | Exception register؛ طلب رسمي؛ تحليل بديل؛ موافقة موقعة؛ سجل الإغلاق. | Regulatory / gate compliance | INDICATOR TEST — نسبة الاستثناءات ذات ملف مكتمل وموافقة مكتوبة؛ تتبع الاستثناءات المفتوحة والمانعة. 4 = 100% of applicable essential/mandatory requirements for the indicator test are Verified as satisfied; required approvals/acceptances are current; no material, blocking, or unapproved exception remains. | INDICATOR TEST — نسبة الاستثناءات ذات ملف مكتمل وموافقة مكتوبة؛ تتبع الاستثناءات المفتوحة والمانعة. 3 = all essential/mandatory requirements are satisfied and >=90% of non-critical checklist/record elements are complete; only minor non-material gaps remain; no acceptance-blocking item. | INDICATOR TEST — نسبة الاستثناءات ذات ملف مكتمل وموافقة مكتوبة؛ تتبع الاستثناءات المفتوحة والمانعة. 2 = 70% to <90% of non-critical checklist/record elements are complete OR one material but correctable gap remains; no Verified failure of an essential mandatory requirement. | INDICATOR TEST — نسبة الاستثناءات ذات ملف مكتمل وموافقة مكتوبة؛ تتبع الاستثناءات المفتوحة والمانعة. 1 = >0% to <70% of required elements are complete/satisfied OR multiple material gaps/open approvals remain; the compliance/control is substantially deficient. | INDICATOR TEST — نسبة الاستثناءات ذات ملف مكتمل وموافقة مكتوبة؛ تتبع الاستثناءات المفتوحة والمانعة. 0 = Verified failure/non-compliance of an essential mandatory requirement, rejected/absent required approval, prohibited condition, or required control is absent. | N/A - non-critical indicator | Applicable Authority Having Jurisdiction (AHJ), adopted local code/permit basis and approved interpretations; HRWHPI Candidate Indicator Set V2.1 FINAL FROZEN RELEASED. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-REG-04 | Mandatory | وسم كل درجة حسب مرحلة الإثبات: Preliminary / Verified؛ وعدم ترقية الحالة دون المستند المطلوب. | سجل مرحلة التقييم؛ قائمة الوثائق المطلوبة؛ الموافقات المستلمة؛ سجل التحقق. | Regulatory / gate compliance | INDICATOR TEST — وسم كل درجة حسب مرحلة الإثبات: Preliminary / Verified؛ وعدم ترقية الحالة دون المستند المطلوب. 4 = 100% of applicable essential/mandatory requirements for the indicator test are Verified as satisfied; required approvals/acceptances are current; no material, blocking, or unapproved exception remains. | INDICATOR TEST — وسم كل درجة حسب مرحلة الإثبات: Preliminary / Verified؛ وعدم ترقية الحالة دون المستند المطلوب. 3 = all essential/mandatory requirements are satisfied and >=90% of non-critical checklist/record elements are complete; only minor non-material gaps remain; no acceptance-blocking item. | INDICATOR TEST — وسم كل درجة حسب مرحلة الإثبات: Preliminary / Verified؛ وعدم ترقية الحالة دون المستند المطلوب. 2 = 70% to <90% of non-critical checklist/record elements are complete OR one material but correctable gap remains; no Verified failure of an essential mandatory requirement. | INDICATOR TEST — وسم كل درجة حسب مرحلة الإثبات: Preliminary / Verified؛ وعدم ترقية الحالة دون المستند المطلوب. 1 = >0% to <70% of required elements are complete/satisfied OR multiple material gaps/open approvals remain; the compliance/control is substantially deficient. | INDICATOR TEST — وسم كل درجة حسب مرحلة الإثبات: Preliminary / Verified؛ وعدم ترقية الحالة دون المستند المطلوب. 0 = Verified failure/non-compliance of an essential mandatory requirement, rejected/absent required approval, prohibited condition, or required control is absent. | N/A - non-critical indicator | Applicable Authority Having Jurisdiction (AHJ), adopted local code/permit basis and approved interpretations; HRWHPI Candidate Indicator Set V2.1 FINAL FROZEN RELEASED. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-SIT-01 | Critical Gate | تحقق Pass/Fail من المتطلبات النظامية والمخططات المعتمدة ومسارات الاقتراب للطوارئ. | شهادة استعمال؛ مخطط مساحي؛ موافقات الارتفاع والارتدادات؛ مخطط وصول الإطفاء والإسعاف. | Regulatory / gate compliance | INDICATOR TEST — تحقق Pass/Fail من المتطلبات النظامية والمخططات المعتمدة ومسارات الاقتراب للطوارئ. 4 = 100% of applicable essential/mandatory requirements for the indicator test are Verified as satisfied; required approvals/acceptances are current; no material, blocking, or unapproved exception remains. | INDICATOR TEST — تحقق Pass/Fail من المتطلبات النظامية والمخططات المعتمدة ومسارات الاقتراب للطوارئ. 3 = all essential/mandatory requirements are satisfied and >=90% of non-critical checklist/record elements are complete; only minor non-material gaps remain; no acceptance-blocking item. | INDICATOR TEST — تحقق Pass/Fail من المتطلبات النظامية والمخططات المعتمدة ومسارات الاقتراب للطوارئ. 2 = 70% to <90% of non-critical checklist/record elements are complete OR one material but correctable gap remains; no Verified failure of an essential mandatory requirement. | INDICATOR TEST — تحقق Pass/Fail من المتطلبات النظامية والمخططات المعتمدة ومسارات الاقتراب للطوارئ. 1 = >0% to <70% of required elements are complete/satisfied OR multiple material gaps/open approvals remain; the compliance/control is substantially deficient. | INDICATOR TEST — تحقق Pass/Fail من المتطلبات النظامية والمخططات المعتمدة ومسارات الاقتراب للطوارئ. 0 = Verified failure/non-compliance of an essential mandatory requirement, rejected/absent required approval, prohibited condition, or required control is absent. | INDICATOR GATE TEST — تحقق Pass/Fail من المتطلبات النظامية والمخططات المعتمدة ومسارات الاقتراب للطوارئ. PASS = Verified evidence demonstrates 100% satisfaction of all applicable essential mandatory requirements/approvals in the indicator test, with no blocking item, rejected requirement, or unapproved exception. | Applicable AHJ site/access requirements and project-approved traffic/emergency-access criteria; 2021 International Building Code as benchmark only where applicable; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); 2021 IBC benchmark only where applicable. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-SIT-02 | Critical Gate | عدد/نسبة نقاط التقاطع؛ زمن وصول الإسعاف؛ اختبار swept path ومحاكاة ساعات الذروة. | Site plan؛ traffic study؛ swept-path analysis؛ خطة التشغيل المروري. | Process / completeness / readiness | INDICATOR TEST — عدد/نسبة نقاط التقاطع؛ زمن وصول الإسعاف؛ اختبار swept path ومحاكاة ساعات الذروة. 4 = 100% of the required package, actions, records, tests, and approvals for the indicator are complete, current, traceable, and Verified; critical open items = 0. | INDICATOR TEST — عدد/نسبة نقاط التقاطع؛ زمن وصول الإسعاف؛ اختبار swept path ومحاكاة ساعات الذروة. 3 = >=90% to <100% complete/closed; critical open items = 0; only minor administrative gaps remain and traceability/readiness is not materially impaired. | INDICATOR TEST — عدد/نسبة نقاط التقاطع؛ زمن وصول الإسعاف؛ اختبار swept path ومحاكاة ساعات الذروة. 2 = >=70% to <90% complete/closed OR one material non-critical open item remains; the process is still auditable and a corrective path is defined. | INDICATOR TEST — عدد/نسبة نقاط التقاطع؛ زمن وصول الإسعاف؛ اختبار swept path ومحاكاة ساعات الذروة. 1 = >0% to <70% complete/closed OR multiple material open items/records are missing; closure/readiness is weak or poorly traceable. | INDICATOR TEST — عدد/نسبة نقاط التقاطع؛ زمن وصول الإسعاف؛ اختبار swept path ومحاكاة ساعات الذروة. 0 = the required process/package/control is absent, a required critical action/test is not implemented, or a critical blocking item remains open. | INDICATOR GATE TEST — عدد/نسبة نقاط التقاطع؛ زمن وصول الإسعاف؛ اختبار swept path ومحاكاة ساعات الذروة. PASS = Verified evidence demonstrates 100% completion and successful closure of all critical checklist/actions/tests in the indicator test; critical open items = 0. | Applicable AHJ site/access requirements and project-approved traffic/emergency-access criteria; 2021 International Building Code as benchmark only where applicable; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); 2021 IBC benchmark only where applicable. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-SIT-03 | Critical Gate | مصفوفة مخاطر الموقع + تحقق سعات المرافق مقابل الطلب التصميمي والاحتياطي. | Utility letters؛ load estimates؛ site risk register؛ مخططات الربط. | Regulatory / gate compliance | INDICATOR TEST — مصفوفة مخاطر الموقع + تحقق سعات المرافق مقابل الطلب التصميمي والاحتياطي. 4 = 100% of applicable essential/mandatory requirements for the indicator test are Verified as satisfied; required approvals/acceptances are current; no material, blocking, or unapproved exception remains. | INDICATOR TEST — مصفوفة مخاطر الموقع + تحقق سعات المرافق مقابل الطلب التصميمي والاحتياطي. 3 = all essential/mandatory requirements are satisfied and >=90% of non-critical checklist/record elements are complete; only minor non-material gaps remain; no acceptance-blocking item. | INDICATOR TEST — مصفوفة مخاطر الموقع + تحقق سعات المرافق مقابل الطلب التصميمي والاحتياطي. 2 = 70% to <90% of non-critical checklist/record elements are complete OR one material but correctable gap remains; no Verified failure of an essential mandatory requirement. | INDICATOR TEST — مصفوفة مخاطر الموقع + تحقق سعات المرافق مقابل الطلب التصميمي والاحتياطي. 1 = >0% to <70% of required elements are complete/satisfied OR multiple material gaps/open approvals remain; the compliance/control is substantially deficient. | INDICATOR TEST — مصفوفة مخاطر الموقع + تحقق سعات المرافق مقابل الطلب التصميمي والاحتياطي. 0 = Verified failure/non-compliance of an essential mandatory requirement, rejected/absent required approval, prohibited condition, or required control is absent. | INDICATOR GATE TEST — مصفوفة مخاطر الموقع + تحقق سعات المرافق مقابل الطلب التصميمي والاحتياطي. PASS = Verified evidence demonstrates 100% satisfaction of all applicable essential mandatory requirements/approvals in the indicator test, with no blocking item, rejected requirement, or unapproved exception. | Applicable AHJ site/access requirements and project-approved traffic/emergency-access criteria; 2021 International Building Code as benchmark only where applicable; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); 2021 IBC benchmark only where applicable. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-SIT-04 | Performance | زمن/مسافة المشي؛ نسبة المسار المظلل؛ مؤشرات الراحة الحرارية؛ نقاط عبور المركبات. | خرائط الوصول؛ نمذجة الشمس/الحرارة؛ مسارات الحركة؛ ملاحظات المستخدمين. | Quantitative performance | INDICATOR TEST — زمن/مسافة المشي؛ نسبة المسار المظلل؛ مؤشرات الراحة الحرارية؛ نقاط عبور المركبات. 4 = 100% of the pre-locked required performance target(s) are met or exceeded under the required representative condition(s), with every mandatory minimum satisfied. | INDICATOR TEST — زمن/مسافة المشي؛ نسبة المسار المظلل؛ مؤشرات الراحة الحرارية؛ نقاط عبور المركبات. 3 = every mandatory minimum is satisfied and >=90% of the pre-locked performance targets are met; remaining variance is minor and non-critical. | INDICATOR TEST — زمن/مسافة المشي؛ نسبة المسار المظلل؛ مؤشرات الراحة الحرارية؛ نقاط عبور المركبات. 2 = >=75% to <90% of pre-locked performance targets are met, with material but correctable shortfall(s); no Verified failure of an essential mandatory minimum. | INDICATOR TEST — زمن/مسافة المشي؛ نسبة المسار المظلل؛ مؤشرات الراحة الحرارية؛ نقاط عبور المركبات. 1 = >0% to <75% of pre-locked performance targets are met OR repeated/large material shortfalls remain; performance is poorly controlled. | INDICATOR TEST — زمن/مسافة المشي؛ نسبة المسار المظلل؛ مؤشرات الراحة الحرارية؛ نقاط عبور المركبات. 0 = a Verified essential mandatory minimum fails, the required performance capability is absent, or none of the required target set is demonstrably achieved. | N/A - non-critical indicator | Applicable AHJ site/access requirements and project-approved traffic/emergency-access criteria; 2021 International Building Code as benchmark only where applicable; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); 2021 IBC benchmark only where applicable. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-SIT-05 | Performance | زمن البحث عن موقف؛ مدة الإنزال؛ طول الطابور؛ زمن الوصول من الموقف إلى الخدمة. | Traffic observations؛ parking counts؛ drop-off queue data؛ خرائط الحركة. | Quantitative performance | INDICATOR TEST — زمن البحث عن موقف؛ مدة الإنزال؛ طول الطابور؛ زمن الوصول من الموقف إلى الخدمة. 4 = 100% of the pre-locked required performance target(s) are met or exceeded under the required representative condition(s), with every mandatory minimum satisfied. | INDICATOR TEST — زمن البحث عن موقف؛ مدة الإنزال؛ طول الطابور؛ زمن الوصول من الموقف إلى الخدمة. 3 = every mandatory minimum is satisfied and >=90% of the pre-locked performance targets are met; remaining variance is minor and non-critical. | INDICATOR TEST — زمن البحث عن موقف؛ مدة الإنزال؛ طول الطابور؛ زمن الوصول من الموقف إلى الخدمة. 2 = >=75% to <90% of pre-locked performance targets are met, with material but correctable shortfall(s); no Verified failure of an essential mandatory minimum. | INDICATOR TEST — زمن البحث عن موقف؛ مدة الإنزال؛ طول الطابور؛ زمن الوصول من الموقف إلى الخدمة. 1 = >0% to <75% of pre-locked performance targets are met OR repeated/large material shortfalls remain; performance is poorly controlled. | INDICATOR TEST — زمن البحث عن موقف؛ مدة الإنزال؛ طول الطابور؛ زمن الوصول من الموقف إلى الخدمة. 0 = a Verified essential mandatory minimum fails, the required performance capability is absent, or none of the required target set is demonstrably achieved. | N/A - non-critical indicator | Applicable AHJ site/access requirements and project-approved traffic/emergency-access criteria; 2021 International Building Code as benchmark only where applicable; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); 2021 IBC benchmark only where applicable. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-SPA-01 | Performance | اختبار سيناريو توسع مستقبلي وتحديد القيود والمساحات والاحتياطيات المطلوبة. | Masterplan؛ structural/service reserve strategy؛ future stacking scenarios. | Functional / spatial performance | INDICATOR TEST — اختبار سيناريو توسع مستقبلي وتحديد القيود والمساحات والاحتياطيات المطلوبة. 4 = 100% of required functional/spatial scenarios and relationships pass the pre-locked criteria; all critical clinical/operational pathways pass; no material conflict remains. | INDICATOR TEST — اختبار سيناريو توسع مستقبلي وتحديد القيود والمساحات والاحتياطيات المطلوبة. 3 = all critical pathways pass and >=90% of non-critical scenarios/relationships pass; only minor inefficiencies or non-material conflicts remain. | INDICATOR TEST — اختبار سيناريو توسع مستقبلي وتحديد القيود والمساحات والاحتياطيات المطلوبة. 2 = >=70% to <90% of required scenarios/relationships pass OR one material but correctable functional conflict remains; no unacceptable critical pathway failure. | INDICATOR TEST — اختبار سيناريو توسع مستقبلي وتحديد القيود والمساحات والاحتياطيات المطلوبة. 1 = >0% to <70% of required scenarios/relationships pass OR multiple material adjacency/movement/privacy/flexibility conflicts remain. | INDICATOR TEST — اختبار سيناريو توسع مستقبلي وتحديد القيود والمساحات والاحتياطيات المطلوبة. 0 = an essential functional/clinical pathway fails, or the tested arrangement creates an unacceptable clinical, privacy, access, or operational risk. | N/A - non-critical indicator | Project-approved clinical brief/space program and scenario criteria; CBAHI Hospital Standards as healthcare benchmark where applicable; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-SPA-02 | Performance | اختبار سيناريوهات تحويل غرف/وحدات على شبكة الأعمدة وارتفاع الطابق والروافع والخدمات. | Typical floor plan؛ column grid؛ service zones؛ scenario test drawings. | Functional / spatial performance | INDICATOR TEST — اختبار سيناريوهات تحويل غرف/وحدات على شبكة الأعمدة وارتفاع الطابق والروافع والخدمات. 4 = 100% of required functional/spatial scenarios and relationships pass the pre-locked criteria; all critical clinical/operational pathways pass; no material conflict remains. | INDICATOR TEST — اختبار سيناريوهات تحويل غرف/وحدات على شبكة الأعمدة وارتفاع الطابق والروافع والخدمات. 3 = all critical pathways pass and >=90% of non-critical scenarios/relationships pass; only minor inefficiencies or non-material conflicts remain. | INDICATOR TEST — اختبار سيناريوهات تحويل غرف/وحدات على شبكة الأعمدة وارتفاع الطابق والروافع والخدمات. 2 = >=70% to <90% of required scenarios/relationships pass OR one material but correctable functional conflict remains; no unacceptable critical pathway failure. | INDICATOR TEST — اختبار سيناريوهات تحويل غرف/وحدات على شبكة الأعمدة وارتفاع الطابق والروافع والخدمات. 1 = >0% to <70% of required scenarios/relationships pass OR multiple material adjacency/movement/privacy/flexibility conflicts remain. | INDICATOR TEST — اختبار سيناريوهات تحويل غرف/وحدات على شبكة الأعمدة وارتفاع الطابق والروافع والخدمات. 0 = an essential functional/clinical pathway fails, or the tested arrangement creates an unacceptable clinical, privacy, access, or operational risk. | N/A - non-critical indicator | Project-approved clinical brief/space program and scenario criteria; CBAHI Hospital Standards as healthcare benchmark where applicable; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-SPA-03 | Performance | نسب المساحة الفنية؛ قياس grid/clear spans؛ اختبار تغيير الاستخدام؛ مراجعة احتياطي shafts. | BIM model؛ structural grid؛ core/shaft schedules؛ technical-space calculations. | Functional / spatial performance | INDICATOR TEST — نسب المساحة الفنية؛ قياس grid/clear spans؛ اختبار تغيير الاستخدام؛ مراجعة احتياطي shafts. 4 = 100% of required functional/spatial scenarios and relationships pass the pre-locked criteria; all critical clinical/operational pathways pass; no material conflict remains. | INDICATOR TEST — نسب المساحة الفنية؛ قياس grid/clear spans؛ اختبار تغيير الاستخدام؛ مراجعة احتياطي shafts. 3 = all critical pathways pass and >=90% of non-critical scenarios/relationships pass; only minor inefficiencies or non-material conflicts remain. | INDICATOR TEST — نسب المساحة الفنية؛ قياس grid/clear spans؛ اختبار تغيير الاستخدام؛ مراجعة احتياطي shafts. 2 = >=70% to <90% of required scenarios/relationships pass OR one material but correctable functional conflict remains; no unacceptable critical pathway failure. | INDICATOR TEST — نسب المساحة الفنية؛ قياس grid/clear spans؛ اختبار تغيير الاستخدام؛ مراجعة احتياطي shafts. 1 = >0% to <70% of required scenarios/relationships pass OR multiple material adjacency/movement/privacy/flexibility conflicts remain. | INDICATOR TEST — نسب المساحة الفنية؛ قياس grid/clear spans؛ اختبار تغيير الاستخدام؛ مراجعة احتياطي shafts. 0 = an essential functional/clinical pathway fails, or the tested arrangement creates an unacceptable clinical, privacy, access, or operational risk. | N/A - non-critical indicator | Project-approved clinical brief/space program and scenario criteria; CBAHI Hospital Standards as healthcare benchmark where applicable; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-CLN-01 | Critical Gate | محاكاة زمن رحلة door-to-door أو event-to-destination مع أزمنة الانتظار والنقل الرأسي عند الحاجة. | Functional program؛ route model؛ elevator simulation؛ observed/mock transfer tests. | Functional / spatial performance | INDICATOR TEST — محاكاة زمن رحلة door-to-door أو event-to-destination مع أزمنة الانتظار والنقل الرأسي عند الحاجة. 4 = 100% of required functional/spatial scenarios and relationships pass the pre-locked criteria; all critical clinical/operational pathways pass; no material conflict remains. | INDICATOR TEST — محاكاة زمن رحلة door-to-door أو event-to-destination مع أزمنة الانتظار والنقل الرأسي عند الحاجة. 3 = all critical pathways pass and >=90% of non-critical scenarios/relationships pass; only minor inefficiencies or non-material conflicts remain. | INDICATOR TEST — محاكاة زمن رحلة door-to-door أو event-to-destination مع أزمنة الانتظار والنقل الرأسي عند الحاجة. 2 = >=70% to <90% of required scenarios/relationships pass OR one material but correctable functional conflict remains; no unacceptable critical pathway failure. | INDICATOR TEST — محاكاة زمن رحلة door-to-door أو event-to-destination مع أزمنة الانتظار والنقل الرأسي عند الحاجة. 1 = >0% to <70% of required scenarios/relationships pass OR multiple material adjacency/movement/privacy/flexibility conflicts remain. | INDICATOR TEST — محاكاة زمن رحلة door-to-door أو event-to-destination مع أزمنة الانتظار والنقل الرأسي عند الحاجة. 0 = an essential functional/clinical pathway fails, or the tested arrangement creates an unacceptable clinical, privacy, access, or operational risk. | INDICATOR GATE TEST — محاكاة زمن رحلة door-to-door أو event-to-destination مع أزمنة الانتظار والنقل الرأسي عند الحاجة. PASS = Verified evidence demonstrates that every critical functional/clinical pathway or scenario in the indicator test meets the pre-locked acceptance criterion, with no material safety/privacy/access/cross-flow failure. | Project-approved clinical workflow/adjacency/privacy criteria; CBAHI Hospital Standards as healthcare benchmark where applicable; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-CLN-02 | Mandatory | تحويل العلاقات المطلوبة إلى زمن/مسافة/عدد انتقالات واختبارها في سيناريوات الذروة. | Adjacency matrix؛ stacking plans؛ movement simulation؛ distance/time outputs. | Functional / spatial performance | INDICATOR TEST — تحويل العلاقات المطلوبة إلى زمن/مسافة/عدد انتقالات واختبارها في سيناريوات الذروة. 4 = 100% of required functional/spatial scenarios and relationships pass the pre-locked criteria; all critical clinical/operational pathways pass; no material conflict remains. | INDICATOR TEST — تحويل العلاقات المطلوبة إلى زمن/مسافة/عدد انتقالات واختبارها في سيناريوات الذروة. 3 = all critical pathways pass and >=90% of non-critical scenarios/relationships pass; only minor inefficiencies or non-material conflicts remain. | INDICATOR TEST — تحويل العلاقات المطلوبة إلى زمن/مسافة/عدد انتقالات واختبارها في سيناريوات الذروة. 2 = >=70% to <90% of required scenarios/relationships pass OR one material but correctable functional conflict remains; no unacceptable critical pathway failure. | INDICATOR TEST — تحويل العلاقات المطلوبة إلى زمن/مسافة/عدد انتقالات واختبارها في سيناريوات الذروة. 1 = >0% to <70% of required scenarios/relationships pass OR multiple material adjacency/movement/privacy/flexibility conflicts remain. | INDICATOR TEST — تحويل العلاقات المطلوبة إلى زمن/مسافة/عدد انتقالات واختبارها في سيناريوات الذروة. 0 = an essential functional/clinical pathway fails, or the tested arrangement creates an unacceptable clinical, privacy, access, or operational risk. | N/A - non-critical indicator | Project-approved clinical workflow/adjacency/privacy criteria; CBAHI Hospital Standards as healthcare benchmark where applicable; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-CLN-03 | Critical Gate | نسبة تقاطع المسارات؛ عدد نقاط العبور؛ مسافة الرحلة؛ نسبة استخدام المصاعد المشتركة؛ مستويات التحكم. | Flow maps؛ access-control plan؛ Space Syntax/agent simulation؛ elevator zoning. | Functional / spatial performance | INDICATOR TEST — نسبة تقاطع المسارات؛ عدد نقاط العبور؛ مسافة الرحلة؛ نسبة استخدام المصاعد المشتركة؛ مستويات التحكم. 4 = 100% of required functional/spatial scenarios and relationships pass the pre-locked criteria; all critical clinical/operational pathways pass; no material conflict remains. | INDICATOR TEST — نسبة تقاطع المسارات؛ عدد نقاط العبور؛ مسافة الرحلة؛ نسبة استخدام المصاعد المشتركة؛ مستويات التحكم. 3 = all critical pathways pass and >=90% of non-critical scenarios/relationships pass; only minor inefficiencies or non-material conflicts remain. | INDICATOR TEST — نسبة تقاطع المسارات؛ عدد نقاط العبور؛ مسافة الرحلة؛ نسبة استخدام المصاعد المشتركة؛ مستويات التحكم. 2 = >=70% to <90% of required scenarios/relationships pass OR one material but correctable functional conflict remains; no unacceptable critical pathway failure. | INDICATOR TEST — نسبة تقاطع المسارات؛ عدد نقاط العبور؛ مسافة الرحلة؛ نسبة استخدام المصاعد المشتركة؛ مستويات التحكم. 1 = >0% to <70% of required scenarios/relationships pass OR multiple material adjacency/movement/privacy/flexibility conflicts remain. | INDICATOR TEST — نسبة تقاطع المسارات؛ عدد نقاط العبور؛ مسافة الرحلة؛ نسبة استخدام المصاعد المشتركة؛ مستويات التحكم. 0 = an essential functional/clinical pathway fails, or the tested arrangement creates an unacceptable clinical, privacy, access, or operational risk. | INDICATOR GATE TEST — نسبة تقاطع المسارات؛ عدد نقاط العبور؛ مسافة الرحلة؛ نسبة استخدام المصاعد المشتركة؛ مستويات التحكم. PASS = Verified evidence demonstrates that every critical functional/clinical pathway or scenario in the indicator test meets the pre-locked acceptance criterion, with no material safety/privacy/access/cross-flow failure. | Project-approved clinical workflow/adjacency/privacy criteria; CBAHI Hospital Standards as healthcare benchmark where applicable; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-CLN-04 | Mandatory | تدقيق sightlines؛ privacy breaches؛ access points؛ user review against defined privacy criteria. | Plans/sections؛ visibility analysis؛ access-control schedule؛ user validation. | Functional / spatial performance | INDICATOR TEST — تدقيق sightlines؛ privacy breaches؛ access points؛ user review against defined privacy criteria. 4 = 100% of required functional/spatial scenarios and relationships pass the pre-locked criteria; all critical clinical/operational pathways pass; no material conflict remains. | INDICATOR TEST — تدقيق sightlines؛ privacy breaches؛ access points؛ user review against defined privacy criteria. 3 = all critical pathways pass and >=90% of non-critical scenarios/relationships pass; only minor inefficiencies or non-material conflicts remain. | INDICATOR TEST — تدقيق sightlines؛ privacy breaches؛ access points؛ user review against defined privacy criteria. 2 = >=70% to <90% of required scenarios/relationships pass OR one material but correctable functional conflict remains; no unacceptable critical pathway failure. | INDICATOR TEST — تدقيق sightlines؛ privacy breaches؛ access points؛ user review against defined privacy criteria. 1 = >0% to <70% of required scenarios/relationships pass OR multiple material adjacency/movement/privacy/flexibility conflicts remain. | INDICATOR TEST — تدقيق sightlines؛ privacy breaches؛ access points؛ user review against defined privacy criteria. 0 = an essential functional/clinical pathway fails, or the tested arrangement creates an unacceptable clinical, privacy, access, or operational risk. | N/A - non-critical indicator | Project-approved clinical workflow/adjacency/privacy criteria; CBAHI Hospital Standards as healthcare benchmark where applicable; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-NIC-01 | Critical Gate | قياس/تحقق المتغيرات البيئية الحرجة وفق متطلبات المشروع مع مراجعة الضوضاء والضغط والحرارة والرطوبة وتكامل الخدمات. | Room data sheets؛ MEP calculations؛ commissioning records؛ environmental trend logs. | Environmental / infection-control performance | INDICATOR TEST — قياس/تحقق المتغيرات البيئية الحرجة وفق متطلبات المشروع مع مراجعة الضوضاء والضغط والحرارة والرطوبة وتكامل الخدمات. 4 = 100% of critical environmental/infection-control parameters and controls meet applicable mandatory limits and >=95% of all pre-defined representative observations/control points conform; monitoring is complete. | INDICATOR TEST — قياس/تحقق المتغيرات البيئية الحرجة وفق متطلبات المشروع مع مراجعة الضوضاء والضغط والحرارة والرطوبة وتكامل الخدمات. 3 = 100% of critical mandatory limits are met and >=90% to <95% of all representative observations/control points conform; only isolated corrected non-critical deviations remain. | INDICATOR TEST — قياس/تحقق المتغيرات البيئية الحرجة وفق متطلبات المشروع مع مراجعة الضوضاء والضغط والحرارة والرطوبة وتكامل الخدمات. 2 = no critical mandatory failure is Verified, but >=75% to <90% of observations/control points conform OR one material non-critical deviation/incomplete monitoring gap remains. | INDICATOR TEST — قياس/تحقق المتغيرات البيئية الحرجة وفق متطلبات المشروع مع مراجعة الضوضاء والضغط والحرارة والرطوبة وتكامل الخدمات. 1 = >=50% to <75% conform OR recurrent material deviations/control instability/inadequate monitoring materially affect the intended condition. | INDICATOR TEST — قياس/تحقق المتغيرات البيئية الحرجة وفق متطلبات المشروع مع مراجعة الضوضاء والضغط والحرارة والرطوبة وتكامل الخدمات. 0 = any Verified critical environmental/infection-control minimum or critical control fails, an uncontrolled critical hazard remains, or <50% of representative observations/control points conform. | INDICATOR GATE TEST — قياس/تحقق المتغيرات البيئية الحرجة وفق متطلبات المشروع مع مراجعة الضوضاء والضغط والحرارة والرطوبة وتكامل الخدمات. PASS = Verified evidence demonstrates that every critical environmental/infection-control parameter and control point in the indicator test is within the applicable mandatory limit; no uncontrolled critical hazard remains. | CBAHI Hospital Standards (NICU); ANSI/ASHRAE/ASHE Standard 170-2021 where ventilation/environment applies; project-approved NICU clinical brief; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); ANSI/ASHRAE/ASHE 170-2021 where applicable; CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-VRT-01 | Mandatory | Elevator traffic simulation حسب فئات الرحلات والأحمال والذروة. | Demand assumptions؛ traffic model؛ elevator schedule؛ scenario outputs. | Functional / spatial performance | INDICATOR TEST — Elevator traffic simulation حسب فئات الرحلات والأحمال والذروة. 4 = 100% of required functional/spatial scenarios and relationships pass the pre-locked criteria; all critical clinical/operational pathways pass; no material conflict remains. | INDICATOR TEST — Elevator traffic simulation حسب فئات الرحلات والأحمال والذروة. 3 = all critical pathways pass and >=90% of non-critical scenarios/relationships pass; only minor inefficiencies or non-material conflicts remain. | INDICATOR TEST — Elevator traffic simulation حسب فئات الرحلات والأحمال والذروة. 2 = >=70% to <90% of required scenarios/relationships pass OR one material but correctable functional conflict remains; no unacceptable critical pathway failure. | INDICATOR TEST — Elevator traffic simulation حسب فئات الرحلات والأحمال والذروة. 1 = >0% to <70% of required scenarios/relationships pass OR multiple material adjacency/movement/privacy/flexibility conflicts remain. | INDICATOR TEST — Elevator traffic simulation حسب فئات الرحلات والأحمال والذروة. 0 = an essential functional/clinical pathway fails, or the tested arrangement creates an unacceptable clinical, privacy, access, or operational risk. | N/A - non-critical indicator | Applicable lift/elevator code/AHJ requirements plus project-approved vertical-transport traffic simulation and service-level criteria; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-VRT-02 | Performance | متوسط/percentile wait time وjourney time وhandling capacity حسب نوع الرحلة. | Elevator simulation؛ commissioning data؛ operational logs. | Quantitative performance | INDICATOR TEST — متوسط/percentile wait time وjourney time وhandling capacity حسب نوع الرحلة. 4 = 100% of the pre-locked required performance target(s) are met or exceeded under the required representative condition(s), with every mandatory minimum satisfied. | INDICATOR TEST — متوسط/percentile wait time وjourney time وhandling capacity حسب نوع الرحلة. 3 = every mandatory minimum is satisfied and >=90% of the pre-locked performance targets are met; remaining variance is minor and non-critical. | INDICATOR TEST — متوسط/percentile wait time وjourney time وhandling capacity حسب نوع الرحلة. 2 = >=75% to <90% of pre-locked performance targets are met, with material but correctable shortfall(s); no Verified failure of an essential mandatory minimum. | INDICATOR TEST — متوسط/percentile wait time وjourney time وhandling capacity حسب نوع الرحلة. 1 = >0% to <75% of pre-locked performance targets are met OR repeated/large material shortfalls remain; performance is poorly controlled. | INDICATOR TEST — متوسط/percentile wait time وjourney time وhandling capacity حسب نوع الرحلة. 0 = a Verified essential mandatory minimum fails, the required performance capability is absent, or none of the required target set is demonstrably achieved. | N/A - non-critical indicator | Applicable lift/elevator code/AHJ requirements plus project-approved vertical-transport traffic simulation and service-level criteria; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-VRT-03 | Critical Gate | اختبار فقد مصعد/مجموعة وقياس بقاء السعة والزمن ضمن مستوى خدمة محدد للمسارات الحرجة. | Failure scenarios؛ traffic simulation؛ maintenance isolation plan؛ test records. | Resilience / failure-scenario performance | INDICATOR TEST — اختبار فقد مصعد/مجموعة وقياس بقاء السعة والزمن ضمن مستوى خدمة محدد للمسارات الحرجة. 4 = 100% of the pre-defined normal, credible failure, maintenance, and recovery scenarios required for this indicator pass; critical function is maintained and the locked recovery target is met. | INDICATOR TEST — اختبار فقد مصعد/مجموعة وقياس بقاء السعة والزمن ضمن مستوى خدمة محدد للمسارات الحرجة. 3 = all critical functions and mandatory failover paths are maintained; only minor non-critical margin/timing variance (<=10% beyond the locked target) remains. | INDICATOR TEST — اختبار فقد مصعد/مجموعة وقياس بقاء السعة والزمن ضمن مستوى خدمة محدد للمسارات الحرجة. 2 = critical safety is maintained but one defined non-catastrophic resilience/failover scenario fails OR recovery is >10% to <=25% beyond the locked target; degraded service remains controlled. | INDICATOR TEST — اختبار فقد مصعد/مجموعة وقياس بقاء السعة والزمن ضمن مستوى خدمة محدد للمسارات الحرجة. 1 = critical resilience is materially weak, multiple scenarios fail, or recovery is >25% beyond the locked target; workaround/redundancy is not fully demonstrated. | INDICATOR TEST — اختبار فقد مصعد/مجموعة وقياس بقاء السعة والزمن ضمن مستوى خدمة محدد للمسارات الحرجة. 0 = a defined credible failure/outage causes loss of an essential critical function, unsafe state, or no credible failover/recovery path is demonstrated. | INDICATOR GATE TEST — اختبار فقد مصعد/مجموعة وقياس بقاء السعة والزمن ضمن مستوى خدمة محدد للمسارات الحرجة. PASS = Verified evidence demonstrates that all mandatory normal/failure/failover/recovery scenarios in the indicator test pass, essential critical function is maintained, and no unresolved critical failure remains. | Applicable lift/elevator code/AHJ requirements plus project-approved vertical-transport traffic simulation and service-level criteria; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-VRT-04 | Critical Gate | اختبارات phased failover؛ قياس السعة البديلة وزمن التحويل؛ تحقق مسار الأسرة/الإسعاف. | Test scripts؛ temporary operation plan؛ outage logs؛ rollback plan. | Resilience / failure-scenario performance | INDICATOR TEST — اختبارات phased failover؛ قياس السعة البديلة وزمن التحويل؛ تحقق مسار الأسرة/الإسعاف. 4 = 100% of the pre-defined normal, credible failure, maintenance, and recovery scenarios required for this indicator pass; critical function is maintained and the locked recovery target is met. | INDICATOR TEST — اختبارات phased failover؛ قياس السعة البديلة وزمن التحويل؛ تحقق مسار الأسرة/الإسعاف. 3 = all critical functions and mandatory failover paths are maintained; only minor non-critical margin/timing variance (<=10% beyond the locked target) remains. | INDICATOR TEST — اختبارات phased failover؛ قياس السعة البديلة وزمن التحويل؛ تحقق مسار الأسرة/الإسعاف. 2 = critical safety is maintained but one defined non-catastrophic resilience/failover scenario fails OR recovery is >10% to <=25% beyond the locked target; degraded service remains controlled. | INDICATOR TEST — اختبارات phased failover؛ قياس السعة البديلة وزمن التحويل؛ تحقق مسار الأسرة/الإسعاف. 1 = critical resilience is materially weak, multiple scenarios fail, or recovery is >25% beyond the locked target; workaround/redundancy is not fully demonstrated. | INDICATOR TEST — اختبارات phased failover؛ قياس السعة البديلة وزمن التحويل؛ تحقق مسار الأسرة/الإسعاف. 0 = a defined credible failure/outage causes loss of an essential critical function, unsafe state, or no credible failover/recovery path is demonstrated. | INDICATOR GATE TEST — اختبارات phased failover؛ قياس السعة البديلة وزمن التحويل؛ تحقق مسار الأسرة/الإسعاف. PASS = Verified evidence demonstrates that all mandatory normal/failure/failover/recovery scenarios in the indicator test pass, essential critical function is maintained, and no unresolved critical failure remains. | Applicable lift/elevator code/AHJ requirements plus project-approved vertical-transport traffic simulation and service-level criteria; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-FIR-01 | Critical Gate | تحقق compartment sizes/routes/refuge capacity وإجراءات الانتقال المرحلي. | Fire strategy؛ compartment plans؛ evacuation plan؛ drill/test records. | Regulatory / gate compliance | INDICATOR TEST — تحقق compartment sizes/routes/refuge capacity وإجراءات الانتقال المرحلي. 4 = 100% of applicable essential/mandatory requirements for the indicator test are Verified as satisfied; required approvals/acceptances are current; no material, blocking, or unapproved exception remains. | INDICATOR TEST — تحقق compartment sizes/routes/refuge capacity وإجراءات الانتقال المرحلي. 3 = all essential/mandatory requirements are satisfied and >=90% of non-critical checklist/record elements are complete; only minor non-material gaps remain; no acceptance-blocking item. | INDICATOR TEST — تحقق compartment sizes/routes/refuge capacity وإجراءات الانتقال المرحلي. 2 = 70% to <90% of non-critical checklist/record elements are complete OR one material but correctable gap remains; no Verified failure of an essential mandatory requirement. | INDICATOR TEST — تحقق compartment sizes/routes/refuge capacity وإجراءات الانتقال المرحلي. 1 = >0% to <70% of required elements are complete/satisfied OR multiple material gaps/open approvals remain; the compliance/control is substantially deficient. | INDICATOR TEST — تحقق compartment sizes/routes/refuge capacity وإجراءات الانتقال المرحلي. 0 = Verified failure/non-compliance of an essential mandatory requirement, rejected/absent required approval, prohibited condition, or required control is absent. | INDICATOR GATE TEST — تحقق compartment sizes/routes/refuge capacity وإجراءات الانتقال المرحلي. PASS = Verified evidence demonstrates 100% satisfaction of all applicable essential mandatory requirements/approvals in the indicator test, with no blocking item, rejected requirement, or unapproved exception. | Applicable fire/life-safety code and AHJ-approved fire strategy; 2021 International Building Code as benchmark where applicable; project-approved integrated test/evacuation criteria; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); 2021 IBC benchmark only where applicable. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-FIR-02 | Critical Gate | تحقق travel distance/capacity/door widths/blocked-route scenarios وفق المرجع الساري. | Egress calculations؛ life-safety plans؛ inspection records. | Regulatory / gate compliance | INDICATOR TEST — تحقق travel distance/capacity/door widths/blocked-route scenarios وفق المرجع الساري. 4 = 100% of applicable essential/mandatory requirements for the indicator test are Verified as satisfied; required approvals/acceptances are current; no material, blocking, or unapproved exception remains. | INDICATOR TEST — تحقق travel distance/capacity/door widths/blocked-route scenarios وفق المرجع الساري. 3 = all essential/mandatory requirements are satisfied and >=90% of non-critical checklist/record elements are complete; only minor non-material gaps remain; no acceptance-blocking item. | INDICATOR TEST — تحقق travel distance/capacity/door widths/blocked-route scenarios وفق المرجع الساري. 2 = 70% to <90% of non-critical checklist/record elements are complete OR one material but correctable gap remains; no Verified failure of an essential mandatory requirement. | INDICATOR TEST — تحقق travel distance/capacity/door widths/blocked-route scenarios وفق المرجع الساري. 1 = >0% to <70% of required elements are complete/satisfied OR multiple material gaps/open approvals remain; the compliance/control is substantially deficient. | INDICATOR TEST — تحقق travel distance/capacity/door widths/blocked-route scenarios وفق المرجع الساري. 0 = Verified failure/non-compliance of an essential mandatory requirement, rejected/absent required approval, prohibited condition, or required control is absent. | INDICATOR GATE TEST — تحقق travel distance/capacity/door widths/blocked-route scenarios وفق المرجع الساري. PASS = Verified evidence demonstrates 100% satisfaction of all applicable essential mandatory requirements/approvals in the indicator test, with no blocking item, rejected requirement, or unapproved exception. | Applicable fire/life-safety code and AHJ-approved fire strategy; 2021 International Building Code as benchmark where applicable; project-approved integrated test/evacuation criteria; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); 2021 IBC benchmark only where applicable. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-FIR-03 | Critical Gate | اختبار الضغط/التدفق والدخان لكل سيناريو؛ مقارنة النتائج بمعايير القبول المعتمدة. | Smoke-control basis؛ calculations؛ cause/effect؛ field test reports. | Resilience / failure-scenario performance | INDICATOR TEST — اختبار الضغط/التدفق والدخان لكل سيناريو؛ مقارنة النتائج بمعايير القبول المعتمدة. 4 = 100% of the pre-defined normal, credible failure, maintenance, and recovery scenarios required for this indicator pass; critical function is maintained and the locked recovery target is met. | INDICATOR TEST — اختبار الضغط/التدفق والدخان لكل سيناريو؛ مقارنة النتائج بمعايير القبول المعتمدة. 3 = all critical functions and mandatory failover paths are maintained; only minor non-critical margin/timing variance (<=10% beyond the locked target) remains. | INDICATOR TEST — اختبار الضغط/التدفق والدخان لكل سيناريو؛ مقارنة النتائج بمعايير القبول المعتمدة. 2 = critical safety is maintained but one defined non-catastrophic resilience/failover scenario fails OR recovery is >10% to <=25% beyond the locked target; degraded service remains controlled. | INDICATOR TEST — اختبار الضغط/التدفق والدخان لكل سيناريو؛ مقارنة النتائج بمعايير القبول المعتمدة. 1 = critical resilience is materially weak, multiple scenarios fail, or recovery is >25% beyond the locked target; workaround/redundancy is not fully demonstrated. | INDICATOR TEST — اختبار الضغط/التدفق والدخان لكل سيناريو؛ مقارنة النتائج بمعايير القبول المعتمدة. 0 = a defined credible failure/outage causes loss of an essential critical function, unsafe state, or no credible failover/recovery path is demonstrated. | INDICATOR GATE TEST — اختبار الضغط/التدفق والدخان لكل سيناريو؛ مقارنة النتائج بمعايير القبول المعتمدة. PASS = Verified evidence demonstrates that all mandatory normal/failure/failover/recovery scenarios in the indicator test pass, essential critical function is maintained, and no unresolved critical failure remains. | Applicable fire/life-safety code and AHJ-approved fire strategy; 2021 International Building Code as benchmark where applicable; project-approved integrated test/evacuation criteria; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); 2021 IBC benchmark only where applicable. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-FIR-04 | Critical Gate | نسبة الاختراقات المسجلة والمطابقة؛ نسبة إغلاق المخالفات الحرجة؛ audit بعد التعديلات. | Firestop register؛ door inspection log؛ photos/labels؛ NCR closure. | Process / completeness / readiness | INDICATOR TEST — نسبة الاختراقات المسجلة والمطابقة؛ نسبة إغلاق المخالفات الحرجة؛ audit بعد التعديلات. 4 = 100% of the required package, actions, records, tests, and approvals for the indicator are complete, current, traceable, and Verified; critical open items = 0. | INDICATOR TEST — نسبة الاختراقات المسجلة والمطابقة؛ نسبة إغلاق المخالفات الحرجة؛ audit بعد التعديلات. 3 = >=90% to <100% complete/closed; critical open items = 0; only minor administrative gaps remain and traceability/readiness is not materially impaired. | INDICATOR TEST — نسبة الاختراقات المسجلة والمطابقة؛ نسبة إغلاق المخالفات الحرجة؛ audit بعد التعديلات. 2 = >=70% to <90% complete/closed OR one material non-critical open item remains; the process is still auditable and a corrective path is defined. | INDICATOR TEST — نسبة الاختراقات المسجلة والمطابقة؛ نسبة إغلاق المخالفات الحرجة؛ audit بعد التعديلات. 1 = >0% to <70% complete/closed OR multiple material open items/records are missing; closure/readiness is weak or poorly traceable. | INDICATOR TEST — نسبة الاختراقات المسجلة والمطابقة؛ نسبة إغلاق المخالفات الحرجة؛ audit بعد التعديلات. 0 = the required process/package/control is absent, a required critical action/test is not implemented, or a critical blocking item remains open. | INDICATOR GATE TEST — نسبة الاختراقات المسجلة والمطابقة؛ نسبة إغلاق المخالفات الحرجة؛ audit بعد التعديلات. PASS = Verified evidence demonstrates 100% completion and successful closure of all critical checklist/actions/tests in the indicator test; critical open items = 0. | Applicable fire/life-safety code and AHJ-approved fire strategy; 2021 International Building Code as benchmark where applicable; project-approved integrated test/evacuation criteria; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); 2021 IBC benchmark only where applicable. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-FIR-05 | Critical Gate | Integrated scenario testing مع timestamps ونتيجة Pass/Fail لكل واجهة. | Cause-and-effect matrix؛ IST scripts؛ alarm logs؛ test certificates. | Resilience / failure-scenario performance | INDICATOR TEST — Integrated scenario testing مع timestamps ونتيجة Pass/Fail لكل واجهة. 4 = 100% of the pre-defined normal, credible failure, maintenance, and recovery scenarios required for this indicator pass; critical function is maintained and the locked recovery target is met. | INDICATOR TEST — Integrated scenario testing مع timestamps ونتيجة Pass/Fail لكل واجهة. 3 = all critical functions and mandatory failover paths are maintained; only minor non-critical margin/timing variance (<=10% beyond the locked target) remains. | INDICATOR TEST — Integrated scenario testing مع timestamps ونتيجة Pass/Fail لكل واجهة. 2 = critical safety is maintained but one defined non-catastrophic resilience/failover scenario fails OR recovery is >10% to <=25% beyond the locked target; degraded service remains controlled. | INDICATOR TEST — Integrated scenario testing مع timestamps ونتيجة Pass/Fail لكل واجهة. 1 = critical resilience is materially weak, multiple scenarios fail, or recovery is >25% beyond the locked target; workaround/redundancy is not fully demonstrated. | INDICATOR TEST — Integrated scenario testing مع timestamps ونتيجة Pass/Fail لكل واجهة. 0 = a defined credible failure/outage causes loss of an essential critical function, unsafe state, or no credible failover/recovery path is demonstrated. | INDICATOR GATE TEST — Integrated scenario testing مع timestamps ونتيجة Pass/Fail لكل واجهة. PASS = Verified evidence demonstrates that all mandatory normal/failure/failover/recovery scenarios in the indicator test pass, essential critical function is maintained, and no unresolved critical failure remains. | Applicable fire/life-safety code and AHJ-approved fire strategy; 2021 International Building Code as benchmark where applicable; project-approved integrated test/evacuation criteria; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); 2021 IBC benchmark only where applicable. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-FIR-06 | Critical Gate | تمرين/محاكاة evacuation time حسب compartment والوردية والإشغال مع نقاط توقف سريرية. | Evacuation model؛ drill records؛ scenario assumptions؛ corrective actions. | Resilience / failure-scenario performance | INDICATOR TEST — تمرين/محاكاة evacuation time حسب compartment والوردية والإشغال مع نقاط توقف سريرية. 4 = 100% of the pre-defined normal, credible failure, maintenance, and recovery scenarios required for this indicator pass; critical function is maintained and the locked recovery target is met. | INDICATOR TEST — تمرين/محاكاة evacuation time حسب compartment والوردية والإشغال مع نقاط توقف سريرية. 3 = all critical functions and mandatory failover paths are maintained; only minor non-critical margin/timing variance (<=10% beyond the locked target) remains. | INDICATOR TEST — تمرين/محاكاة evacuation time حسب compartment والوردية والإشغال مع نقاط توقف سريرية. 2 = critical safety is maintained but one defined non-catastrophic resilience/failover scenario fails OR recovery is >10% to <=25% beyond the locked target; degraded service remains controlled. | INDICATOR TEST — تمرين/محاكاة evacuation time حسب compartment والوردية والإشغال مع نقاط توقف سريرية. 1 = critical resilience is materially weak, multiple scenarios fail, or recovery is >25% beyond the locked target; workaround/redundancy is not fully demonstrated. | INDICATOR TEST — تمرين/محاكاة evacuation time حسب compartment والوردية والإشغال مع نقاط توقف سريرية. 0 = a defined credible failure/outage causes loss of an essential critical function, unsafe state, or no credible failover/recovery path is demonstrated. | INDICATOR GATE TEST — تمرين/محاكاة evacuation time حسب compartment والوردية والإشغال مع نقاط توقف سريرية. PASS = Verified evidence demonstrates that all mandatory normal/failure/failover/recovery scenarios in the indicator test pass, essential critical function is maintained, and no unresolved critical failure remains. | Applicable fire/life-safety code and AHJ-approved fire strategy; 2021 International Building Code as benchmark where applicable; project-approved integrated test/evacuation criteria; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); 2021 IBC benchmark only where applicable. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-MEP-01 | Critical Gate | اختبار فقد المصدر والتحويل للمولد/UPS وقياس زمن الاستعادة والأحمال غير المخدومة. | Single-line؛ load schedules؛ generator/UPS tests؛ failover logs. | Resilience / failure-scenario performance | INDICATOR TEST — اختبار فقد المصدر والتحويل للمولد/UPS وقياس زمن الاستعادة والأحمال غير المخدومة. 4 = 100% of the pre-defined normal, credible failure, maintenance, and recovery scenarios required for this indicator pass; critical function is maintained and the locked recovery target is met. | INDICATOR TEST — اختبار فقد المصدر والتحويل للمولد/UPS وقياس زمن الاستعادة والأحمال غير المخدومة. 3 = all critical functions and mandatory failover paths are maintained; only minor non-critical margin/timing variance (<=10% beyond the locked target) remains. | INDICATOR TEST — اختبار فقد المصدر والتحويل للمولد/UPS وقياس زمن الاستعادة والأحمال غير المخدومة. 2 = critical safety is maintained but one defined non-catastrophic resilience/failover scenario fails OR recovery is >10% to <=25% beyond the locked target; degraded service remains controlled. | INDICATOR TEST — اختبار فقد المصدر والتحويل للمولد/UPS وقياس زمن الاستعادة والأحمال غير المخدومة. 1 = critical resilience is materially weak, multiple scenarios fail, or recovery is >25% beyond the locked target; workaround/redundancy is not fully demonstrated. | INDICATOR TEST — اختبار فقد المصدر والتحويل للمولد/UPS وقياس زمن الاستعادة والأحمال غير المخدومة. 0 = a defined credible failure/outage causes loss of an essential critical function, unsafe state, or no credible failover/recovery path is demonstrated. | INDICATOR GATE TEST — اختبار فقد المصدر والتحويل للمولد/UPS وقياس زمن الاستعادة والأحمال غير المخدومة. PASS = Verified evidence demonstrates that all mandatory normal/failure/failover/recovery scenarios in the indicator test pass, essential critical function is maintained, and no unresolved critical failure remains. | Applicable MEP/electrical/medical-gas/water codes and approved project engineering criteria; ANSI/ASHRAE/ASHE Standard 170-2021 where HVAC applies; CBAHI Hospital Standards; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); ANSI/ASHRAE/ASHE 170-2021 where applicable; CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-MEP-02 | Critical Gate | Trend/field measurement في normal/failure modes؛ زمن الاستعادة بعد الاضطراب. | TAB؛ commissioning؛ BMS trends؛ pressure/temperature/humidity logs. | Resilience / failure-scenario performance | INDICATOR TEST — Trend/field measurement في normal/failure modes؛ زمن الاستعادة بعد الاضطراب. 4 = 100% of the pre-defined normal, credible failure, maintenance, and recovery scenarios required for this indicator pass; critical function is maintained and the locked recovery target is met. | INDICATOR TEST — Trend/field measurement في normal/failure modes؛ زمن الاستعادة بعد الاضطراب. 3 = all critical functions and mandatory failover paths are maintained; only minor non-critical margin/timing variance (<=10% beyond the locked target) remains. | INDICATOR TEST — Trend/field measurement في normal/failure modes؛ زمن الاستعادة بعد الاضطراب. 2 = critical safety is maintained but one defined non-catastrophic resilience/failover scenario fails OR recovery is >10% to <=25% beyond the locked target; degraded service remains controlled. | INDICATOR TEST — Trend/field measurement في normal/failure modes؛ زمن الاستعادة بعد الاضطراب. 1 = critical resilience is materially weak, multiple scenarios fail, or recovery is >25% beyond the locked target; workaround/redundancy is not fully demonstrated. | INDICATOR TEST — Trend/field measurement في normal/failure modes؛ زمن الاستعادة بعد الاضطراب. 0 = a defined credible failure/outage causes loss of an essential critical function, unsafe state, or no credible failover/recovery path is demonstrated. | INDICATOR GATE TEST — Trend/field measurement في normal/failure modes؛ زمن الاستعادة بعد الاضطراب. PASS = Verified evidence demonstrates that all mandatory normal/failure/failover/recovery scenarios in the indicator test pass, essential critical function is maintained, and no unresolved critical failure remains. | Applicable MEP/electrical/medical-gas/water codes and approved project engineering criteria; ANSI/ASHRAE/ASHE Standard 170-2021 where HVAC applies; CBAHI Hospital Standards; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); ANSI/ASHRAE/ASHE 170-2021 where applicable; CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-MEP-03 | Critical Gate | اختبارات pressure/purity/alarm/failover؛ زمن الاستعادة؛ تحقق source redundancy. | Medical-gas certification؛ alarm tests؛ zone-valve plan؛ failover records. | Resilience / failure-scenario performance | INDICATOR TEST — اختبارات pressure/purity/alarm/failover؛ زمن الاستعادة؛ تحقق source redundancy. 4 = 100% of the pre-defined normal, credible failure, maintenance, and recovery scenarios required for this indicator pass; critical function is maintained and the locked recovery target is met. | INDICATOR TEST — اختبارات pressure/purity/alarm/failover؛ زمن الاستعادة؛ تحقق source redundancy. 3 = all critical functions and mandatory failover paths are maintained; only minor non-critical margin/timing variance (<=10% beyond the locked target) remains. | INDICATOR TEST — اختبارات pressure/purity/alarm/failover؛ زمن الاستعادة؛ تحقق source redundancy. 2 = critical safety is maintained but one defined non-catastrophic resilience/failover scenario fails OR recovery is >10% to <=25% beyond the locked target; degraded service remains controlled. | INDICATOR TEST — اختبارات pressure/purity/alarm/failover؛ زمن الاستعادة؛ تحقق source redundancy. 1 = critical resilience is materially weak, multiple scenarios fail, or recovery is >25% beyond the locked target; workaround/redundancy is not fully demonstrated. | INDICATOR TEST — اختبارات pressure/purity/alarm/failover؛ زمن الاستعادة؛ تحقق source redundancy. 0 = a defined credible failure/outage causes loss of an essential critical function, unsafe state, or no credible failover/recovery path is demonstrated. | INDICATOR GATE TEST — اختبارات pressure/purity/alarm/failover؛ زمن الاستعادة؛ تحقق source redundancy. PASS = Verified evidence demonstrates that all mandatory normal/failure/failover/recovery scenarios in the indicator test pass, essential critical function is maintained, and no unresolved critical failure remains. | Applicable MEP/electrical/medical-gas/water codes and approved project engineering criteria; ANSI/ASHRAE/ASHE Standard 170-2021 where HVAC applies; CBAHI Hospital Standards; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); ANSI/ASHRAE/ASHE 170-2021 where applicable; CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-MEP-04 | Critical Gate | اختبار redundancy/isolation/backflow؛ زمن الاستجابة للتسرب؛ تحقق سعة الضغط والصرف. | P&ID؛ water-quality records؛ backflow tests؛ incident/repair logs. | Resilience / failure-scenario performance | INDICATOR TEST — اختبار redundancy/isolation/backflow؛ زمن الاستجابة للتسرب؛ تحقق سعة الضغط والصرف. 4 = 100% of the pre-defined normal, credible failure, maintenance, and recovery scenarios required for this indicator pass; critical function is maintained and the locked recovery target is met. | INDICATOR TEST — اختبار redundancy/isolation/backflow؛ زمن الاستجابة للتسرب؛ تحقق سعة الضغط والصرف. 3 = all critical functions and mandatory failover paths are maintained; only minor non-critical margin/timing variance (<=10% beyond the locked target) remains. | INDICATOR TEST — اختبار redundancy/isolation/backflow؛ زمن الاستجابة للتسرب؛ تحقق سعة الضغط والصرف. 2 = critical safety is maintained but one defined non-catastrophic resilience/failover scenario fails OR recovery is >10% to <=25% beyond the locked target; degraded service remains controlled. | INDICATOR TEST — اختبار redundancy/isolation/backflow؛ زمن الاستجابة للتسرب؛ تحقق سعة الضغط والصرف. 1 = critical resilience is materially weak, multiple scenarios fail, or recovery is >25% beyond the locked target; workaround/redundancy is not fully demonstrated. | INDICATOR TEST — اختبار redundancy/isolation/backflow؛ زمن الاستجابة للتسرب؛ تحقق سعة الضغط والصرف. 0 = a defined credible failure/outage causes loss of an essential critical function, unsafe state, or no credible failover/recovery path is demonstrated. | INDICATOR GATE TEST — اختبار redundancy/isolation/backflow؛ زمن الاستجابة للتسرب؛ تحقق سعة الضغط والصرف. PASS = Verified evidence demonstrates that all mandatory normal/failure/failover/recovery scenarios in the indicator test pass, essential critical function is maintained, and no unresolved critical failure remains. | Applicable MEP/electrical/medical-gas/water codes and approved project engineering criteria; ANSI/ASHRAE/ASHE Standard 170-2021 where HVAC applies; CBAHI Hospital Standards; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); ANSI/ASHRAE/ASHE 170-2021 where applicable; CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-RES-01 | Performance | حساب availability وMTTR وrecovery time لكل نظام حرج خلال فترة محددة. | CMMS/BMS logs؛ incident records؛ failure-test reports. | Quantitative performance | INDICATOR TEST — حساب availability وMTTR وrecovery time لكل نظام حرج خلال فترة محددة. 4 = 100% of the pre-locked required performance target(s) are met or exceeded under the required representative condition(s), with every mandatory minimum satisfied. | INDICATOR TEST — حساب availability وMTTR وrecovery time لكل نظام حرج خلال فترة محددة. 3 = every mandatory minimum is satisfied and >=90% of the pre-locked performance targets are met; remaining variance is minor and non-critical. | INDICATOR TEST — حساب availability وMTTR وrecovery time لكل نظام حرج خلال فترة محددة. 2 = >=75% to <90% of pre-locked performance targets are met, with material but correctable shortfall(s); no Verified failure of an essential mandatory minimum. | INDICATOR TEST — حساب availability وMTTR وrecovery time لكل نظام حرج خلال فترة محددة. 1 = >0% to <75% of pre-locked performance targets are met OR repeated/large material shortfalls remain; performance is poorly controlled. | INDICATOR TEST — حساب availability وMTTR وrecovery time لكل نظام حرج خلال فترة محددة. 0 = a Verified essential mandatory minimum fails, the required performance capability is absent, or none of the required target set is demonstrably achieved. | N/A - non-critical indicator | Project-approved resilience/FMEA/commissioning criteria and applicable critical-system requirements; CBAHI Hospital Standards; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-RES-02 | Critical Gate | FMEA + isolation/failover test؛ تحقق فقد عنصر منفرد دون فقد الوظيفة الحرجة المحددة. | FMEA؛ zoning/isolation drawings؛ failover test؛ maintenance method. | Resilience / failure-scenario performance | INDICATOR TEST — FMEA + isolation/failover test؛ تحقق فقد عنصر منفرد دون فقد الوظيفة الحرجة المحددة. 4 = 100% of the pre-defined normal, credible failure, maintenance, and recovery scenarios required for this indicator pass; critical function is maintained and the locked recovery target is met. | INDICATOR TEST — FMEA + isolation/failover test؛ تحقق فقد عنصر منفرد دون فقد الوظيفة الحرجة المحددة. 3 = all critical functions and mandatory failover paths are maintained; only minor non-critical margin/timing variance (<=10% beyond the locked target) remains. | INDICATOR TEST — FMEA + isolation/failover test؛ تحقق فقد عنصر منفرد دون فقد الوظيفة الحرجة المحددة. 2 = critical safety is maintained but one defined non-catastrophic resilience/failover scenario fails OR recovery is >10% to <=25% beyond the locked target; degraded service remains controlled. | INDICATOR TEST — FMEA + isolation/failover test؛ تحقق فقد عنصر منفرد دون فقد الوظيفة الحرجة المحددة. 1 = critical resilience is materially weak, multiple scenarios fail, or recovery is >25% beyond the locked target; workaround/redundancy is not fully demonstrated. | INDICATOR TEST — FMEA + isolation/failover test؛ تحقق فقد عنصر منفرد دون فقد الوظيفة الحرجة المحددة. 0 = a defined credible failure/outage causes loss of an essential critical function, unsafe state, or no credible failover/recovery path is demonstrated. | INDICATOR GATE TEST — FMEA + isolation/failover test؛ تحقق فقد عنصر منفرد دون فقد الوظيفة الحرجة المحددة. PASS = Verified evidence demonstrates that all mandatory normal/failure/failover/recovery scenarios in the indicator test pass, essential critical function is maintained, and no unresolved critical failure remains. | Project-approved resilience/FMEA/commissioning criteria and applicable critical-system requirements; CBAHI Hospital Standards; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-RES-03 | Mandatory | سيناريوات tabletop ثم staged integrated tests؛ قياس استمرارية الوظائف وزمن الاستعادة. | Hazard register؛ emergency scripts؛ IST records؛ corrective-action log. | Process / completeness / readiness | INDICATOR TEST — سيناريوات tabletop ثم staged integrated tests؛ قياس استمرارية الوظائف وزمن الاستعادة. 4 = 100% of the required package, actions, records, tests, and approvals for the indicator are complete, current, traceable, and Verified; critical open items = 0. | INDICATOR TEST — سيناريوات tabletop ثم staged integrated tests؛ قياس استمرارية الوظائف وزمن الاستعادة. 3 = >=90% to <100% complete/closed; critical open items = 0; only minor administrative gaps remain and traceability/readiness is not materially impaired. | INDICATOR TEST — سيناريوات tabletop ثم staged integrated tests؛ قياس استمرارية الوظائف وزمن الاستعادة. 2 = >=70% to <90% complete/closed OR one material non-critical open item remains; the process is still auditable and a corrective path is defined. | INDICATOR TEST — سيناريوات tabletop ثم staged integrated tests؛ قياس استمرارية الوظائف وزمن الاستعادة. 1 = >0% to <70% complete/closed OR multiple material open items/records are missing; closure/readiness is weak or poorly traceable. | INDICATOR TEST — سيناريوات tabletop ثم staged integrated tests؛ قياس استمرارية الوظائف وزمن الاستعادة. 0 = the required process/package/control is absent, a required critical action/test is not implemented, or a critical blocking item remains open. | N/A - non-critical indicator | Project-approved resilience/FMEA/commissioning criteria and applicable critical-system requirements; CBAHI Hospital Standards; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-RES-04 | Critical Gate | Failure injection / simulated outage؛ زمن التحويل والاستعادة؛ Pass/Fail حسب سيناريو متفق عليه. | Test script؛ outage log؛ failover sequence؛ rollback plan؛ sign-off. | Resilience / failure-scenario performance | INDICATOR TEST — Failure injection / simulated outage؛ زمن التحويل والاستعادة؛ Pass/Fail حسب سيناريو متفق عليه. 4 = 100% of the pre-defined normal, credible failure, maintenance, and recovery scenarios required for this indicator pass; critical function is maintained and the locked recovery target is met. | INDICATOR TEST — Failure injection / simulated outage؛ زمن التحويل والاستعادة؛ Pass/Fail حسب سيناريو متفق عليه. 3 = all critical functions and mandatory failover paths are maintained; only minor non-critical margin/timing variance (<=10% beyond the locked target) remains. | INDICATOR TEST — Failure injection / simulated outage؛ زمن التحويل والاستعادة؛ Pass/Fail حسب سيناريو متفق عليه. 2 = critical safety is maintained but one defined non-catastrophic resilience/failover scenario fails OR recovery is >10% to <=25% beyond the locked target; degraded service remains controlled. | INDICATOR TEST — Failure injection / simulated outage؛ زمن التحويل والاستعادة؛ Pass/Fail حسب سيناريو متفق عليه. 1 = critical resilience is materially weak, multiple scenarios fail, or recovery is >25% beyond the locked target; workaround/redundancy is not fully demonstrated. | INDICATOR TEST — Failure injection / simulated outage؛ زمن التحويل والاستعادة؛ Pass/Fail حسب سيناريو متفق عليه. 0 = a defined credible failure/outage causes loss of an essential critical function, unsafe state, or no credible failover/recovery path is demonstrated. | INDICATOR GATE TEST — Failure injection / simulated outage؛ زمن التحويل والاستعادة؛ Pass/Fail حسب سيناريو متفق عليه. PASS = Verified evidence demonstrates that all mandatory normal/failure/failover/recovery scenarios in the indicator test pass, essential critical function is maintained, and no unresolved critical failure remains. | Project-approved resilience/FMEA/commissioning criteria and applicable critical-system requirements; CBAHI Hospital Standards; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-ENV-01 | Critical Gate | Audit تنفيذ ICRA حسب المرحلة؛ قياسات الضغط/الجسيمات؛ حوادث الاختراق؛ إغلاق المخالفات. | ICRA forms؛ barrier/pressure logs؛ particle monitoring؛ cleaning records. | Environmental / infection-control performance | INDICATOR TEST — Audit تنفيذ ICRA حسب المرحلة؛ قياسات الضغط/الجسيمات؛ حوادث الاختراق؛ إغلاق المخالفات. 4 = 100% of critical environmental/infection-control parameters and controls meet applicable mandatory limits and >=95% of all pre-defined representative observations/control points conform; monitoring is complete. | INDICATOR TEST — Audit تنفيذ ICRA حسب المرحلة؛ قياسات الضغط/الجسيمات؛ حوادث الاختراق؛ إغلاق المخالفات. 3 = 100% of critical mandatory limits are met and >=90% to <95% of all representative observations/control points conform; only isolated corrected non-critical deviations remain. | INDICATOR TEST — Audit تنفيذ ICRA حسب المرحلة؛ قياسات الضغط/الجسيمات؛ حوادث الاختراق؛ إغلاق المخالفات. 2 = no critical mandatory failure is Verified, but >=75% to <90% of observations/control points conform OR one material non-critical deviation/incomplete monitoring gap remains. | INDICATOR TEST — Audit تنفيذ ICRA حسب المرحلة؛ قياسات الضغط/الجسيمات؛ حوادث الاختراق؛ إغلاق المخالفات. 1 = >=50% to <75% conform OR recurrent material deviations/control instability/inadequate monitoring materially affect the intended condition. | INDICATOR TEST — Audit تنفيذ ICRA حسب المرحلة؛ قياسات الضغط/الجسيمات؛ حوادث الاختراق؛ إغلاق المخالفات. 0 = any Verified critical environmental/infection-control minimum or critical control fails, an uncontrolled critical hazard remains, or <50% of representative observations/control points conform. | INDICATOR GATE TEST — Audit تنفيذ ICRA حسب المرحلة؛ قياسات الضغط/الجسيمات؛ حوادث الاختراق؛ إغلاق المخالفات. PASS = Verified evidence demonstrates that every critical environmental/infection-control parameter and control point in the indicator test is within the applicable mandatory limit; no uncontrolled critical hazard remains. | ANSI/ASHRAE/ASHE Standard 170-2021; WELL Building Standard v2 Q4 2020 as benchmark; IFC Performance Standards effective 2012 PS3/PS4 as risk/performance benchmark; CBAHI infection-control requirements; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); ANSI/ASHRAE/ASHE 170-2021 where applicable; WELL v2 Q4 2020 benchmark; IFC PS (effective 2012) PS3/PS4 benchmark. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-ENV-02 | Mandatory | تتبع route intersections؛ storage capacity؛ room ventilation/temperature؛ audit نقاط النقل. | Waste plan؛ linen/cleaning routes؛ storage room data؛ operational audit. | Environmental / infection-control performance | INDICATOR TEST — تتبع route intersections؛ storage capacity؛ room ventilation/temperature؛ audit نقاط النقل. 4 = 100% of critical environmental/infection-control parameters and controls meet applicable mandatory limits and >=95% of all pre-defined representative observations/control points conform; monitoring is complete. | INDICATOR TEST — تتبع route intersections؛ storage capacity؛ room ventilation/temperature؛ audit نقاط النقل. 3 = 100% of critical mandatory limits are met and >=90% to <95% of all representative observations/control points conform; only isolated corrected non-critical deviations remain. | INDICATOR TEST — تتبع route intersections؛ storage capacity؛ room ventilation/temperature؛ audit نقاط النقل. 2 = no critical mandatory failure is Verified, but >=75% to <90% of observations/control points conform OR one material non-critical deviation/incomplete monitoring gap remains. | INDICATOR TEST — تتبع route intersections؛ storage capacity؛ room ventilation/temperature؛ audit نقاط النقل. 1 = >=50% to <75% conform OR recurrent material deviations/control instability/inadequate monitoring materially affect the intended condition. | INDICATOR TEST — تتبع route intersections؛ storage capacity؛ room ventilation/temperature؛ audit نقاط النقل. 0 = any Verified critical environmental/infection-control minimum or critical control fails, an uncontrolled critical hazard remains, or <50% of representative observations/control points conform. | N/A - non-critical indicator | ANSI/ASHRAE/ASHE Standard 170-2021; WELL Building Standard v2 Q4 2020 as benchmark; IFC Performance Standards effective 2012 PS3/PS4 as risk/performance benchmark; CBAHI infection-control requirements; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); ANSI/ASHRAE/ASHE 170-2021 where applicable; WELL v2 Q4 2020 benchmark; IFC PS (effective 2012) PS3/PS4 benchmark. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-ENV-03 | Critical Gate | تحليل source-to-intake separation + wind/dispersion study أو قياس عند الحاجة. | Site pollution map؛ intake locations؛ wind study؛ air-quality measurements. | Environmental / infection-control performance | INDICATOR TEST — تحليل source-to-intake separation + wind/dispersion study أو قياس عند الحاجة. 4 = 100% of critical environmental/infection-control parameters and controls meet applicable mandatory limits and >=95% of all pre-defined representative observations/control points conform; monitoring is complete. | INDICATOR TEST — تحليل source-to-intake separation + wind/dispersion study أو قياس عند الحاجة. 3 = 100% of critical mandatory limits are met and >=90% to <95% of all representative observations/control points conform; only isolated corrected non-critical deviations remain. | INDICATOR TEST — تحليل source-to-intake separation + wind/dispersion study أو قياس عند الحاجة. 2 = no critical mandatory failure is Verified, but >=75% to <90% of observations/control points conform OR one material non-critical deviation/incomplete monitoring gap remains. | INDICATOR TEST — تحليل source-to-intake separation + wind/dispersion study أو قياس عند الحاجة. 1 = >=50% to <75% conform OR recurrent material deviations/control instability/inadequate monitoring materially affect the intended condition. | INDICATOR TEST — تحليل source-to-intake separation + wind/dispersion study أو قياس عند الحاجة. 0 = any Verified critical environmental/infection-control minimum or critical control fails, an uncontrolled critical hazard remains, or <50% of representative observations/control points conform. | INDICATOR GATE TEST — تحليل source-to-intake separation + wind/dispersion study أو قياس عند الحاجة. PASS = Verified evidence demonstrates that every critical environmental/infection-control parameter and control point in the indicator test is within the applicable mandatory limit; no uncontrolled critical hazard remains. | ANSI/ASHRAE/ASHE Standard 170-2021; WELL Building Standard v2 Q4 2020 as benchmark; IFC Performance Standards effective 2012 PS3/PS4 as risk/performance benchmark; CBAHI infection-control requirements; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); ANSI/ASHRAE/ASHE 170-2021 where applicable; WELL v2 Q4 2020 benchmark; IFC PS (effective 2012) PS3/PS4 benchmark. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-ENV-04 | Performance | مؤشرات التعرض الحراري/الغبار/الضوضاء حسب نقاط استخدام محددة ومواسم التشغيل. | Environmental study؛ climate model؛ sensor/monitoring data؛ mitigation plan. | Environmental / infection-control performance | INDICATOR TEST — مؤشرات التعرض الحراري/الغبار/الضوضاء حسب نقاط استخدام محددة ومواسم التشغيل. 4 = 100% of critical environmental/infection-control parameters and controls meet applicable mandatory limits and >=95% of all pre-defined representative observations/control points conform; monitoring is complete. | INDICATOR TEST — مؤشرات التعرض الحراري/الغبار/الضوضاء حسب نقاط استخدام محددة ومواسم التشغيل. 3 = 100% of critical mandatory limits are met and >=90% to <95% of all representative observations/control points conform; only isolated corrected non-critical deviations remain. | INDICATOR TEST — مؤشرات التعرض الحراري/الغبار/الضوضاء حسب نقاط استخدام محددة ومواسم التشغيل. 2 = no critical mandatory failure is Verified, but >=75% to <90% of observations/control points conform OR one material non-critical deviation/incomplete monitoring gap remains. | INDICATOR TEST — مؤشرات التعرض الحراري/الغبار/الضوضاء حسب نقاط استخدام محددة ومواسم التشغيل. 1 = >=50% to <75% conform OR recurrent material deviations/control instability/inadequate monitoring materially affect the intended condition. | INDICATOR TEST — مؤشرات التعرض الحراري/الغبار/الضوضاء حسب نقاط استخدام محددة ومواسم التشغيل. 0 = any Verified critical environmental/infection-control minimum or critical control fails, an uncontrolled critical hazard remains, or <50% of representative observations/control points conform. | N/A - non-critical indicator | ANSI/ASHRAE/ASHE Standard 170-2021; WELL Building Standard v2 Q4 2020 as benchmark; IFC Performance Standards effective 2012 PS3/PS4 as risk/performance benchmark; CBAHI infection-control requirements; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); ANSI/ASHRAE/ASHE 170-2021 where applicable; WELL v2 Q4 2020 benchmark; IFC PS (effective 2012) PS3/PS4 benchmark. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-ENV-05 | Performance | Audit score؛ cleaning defects/incidents؛ response/closure time؛ repeat issues. | Cleaning logs؛ audit reports؛ incident/complaint records. | Environmental / infection-control performance | INDICATOR TEST — Audit score؛ cleaning defects/incidents؛ response/closure time؛ repeat issues. 4 = 100% of critical environmental/infection-control parameters and controls meet applicable mandatory limits and >=95% of all pre-defined representative observations/control points conform; monitoring is complete. | INDICATOR TEST — Audit score؛ cleaning defects/incidents؛ response/closure time؛ repeat issues. 3 = 100% of critical mandatory limits are met and >=90% to <95% of all representative observations/control points conform; only isolated corrected non-critical deviations remain. | INDICATOR TEST — Audit score؛ cleaning defects/incidents؛ response/closure time؛ repeat issues. 2 = no critical mandatory failure is Verified, but >=75% to <90% of observations/control points conform OR one material non-critical deviation/incomplete monitoring gap remains. | INDICATOR TEST — Audit score؛ cleaning defects/incidents؛ response/closure time؛ repeat issues. 1 = >=50% to <75% conform OR recurrent material deviations/control instability/inadequate monitoring materially affect the intended condition. | INDICATOR TEST — Audit score؛ cleaning defects/incidents؛ response/closure time؛ repeat issues. 0 = any Verified critical environmental/infection-control minimum or critical control fails, an uncontrolled critical hazard remains, or <50% of representative observations/control points conform. | N/A - non-critical indicator | ANSI/ASHRAE/ASHE Standard 170-2021; WELL Building Standard v2 Q4 2020 as benchmark; IFC Performance Standards effective 2012 PS3/PS4 as risk/performance benchmark; CBAHI infection-control requirements; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); ANSI/ASHRAE/ASHE 170-2021 where applicable; WELL v2 Q4 2020 benchmark; IFC PS (effective 2012) PS3/PS4 benchmark. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-ENV-06 | Enhancement | Daylight/solar/thermal simulation + glare and sightline checks for representative rooms. | Daylight model؛ thermal model؛ façade data؛ view/privacy analysis. | Environmental / infection-control performance | INDICATOR TEST — Daylight/solar/thermal simulation + glare and sightline checks for representative rooms. 4 = 100% of critical environmental/infection-control parameters and controls meet applicable mandatory limits and >=95% of all pre-defined representative observations/control points conform; monitoring is complete. | INDICATOR TEST — Daylight/solar/thermal simulation + glare and sightline checks for representative rooms. 3 = 100% of critical mandatory limits are met and >=90% to <95% of all representative observations/control points conform; only isolated corrected non-critical deviations remain. | INDICATOR TEST — Daylight/solar/thermal simulation + glare and sightline checks for representative rooms. 2 = no critical mandatory failure is Verified, but >=75% to <90% of observations/control points conform OR one material non-critical deviation/incomplete monitoring gap remains. | INDICATOR TEST — Daylight/solar/thermal simulation + glare and sightline checks for representative rooms. 1 = >=50% to <75% conform OR recurrent material deviations/control instability/inadequate monitoring materially affect the intended condition. | INDICATOR TEST — Daylight/solar/thermal simulation + glare and sightline checks for representative rooms. 0 = any Verified critical environmental/infection-control minimum or critical control fails, an uncontrolled critical hazard remains, or <50% of representative observations/control points conform. | N/A - non-critical indicator | ANSI/ASHRAE/ASHE Standard 170-2021; WELL Building Standard v2 Q4 2020 as benchmark; IFC Performance Standards effective 2012 PS3/PS4 as risk/performance benchmark; CBAHI infection-control requirements; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); ANSI/ASHRAE/ASHE 170-2021 where applicable; WELL v2 Q4 2020 benchmark; IFC PS (effective 2012) PS3/PS4 benchmark. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-CON-01 | Mandatory | Open-clash density؛ RFI closure before work؛ shop-drawing completeness؛ access checks. | Federated BIM؛ clash report؛ RFI log؛ shop drawings؛ constructability reviews. | Process / completeness / readiness | INDICATOR TEST — Open-clash density؛ RFI closure before work؛ shop-drawing completeness؛ access checks. 4 = 100% of the required package, actions, records, tests, and approvals for the indicator are complete, current, traceable, and Verified; critical open items = 0. | INDICATOR TEST — Open-clash density؛ RFI closure before work؛ shop-drawing completeness؛ access checks. 3 = >=90% to <100% complete/closed; critical open items = 0; only minor administrative gaps remain and traceability/readiness is not materially impaired. | INDICATOR TEST — Open-clash density؛ RFI closure before work؛ shop-drawing completeness؛ access checks. 2 = >=70% to <90% complete/closed OR one material non-critical open item remains; the process is still auditable and a corrective path is defined. | INDICATOR TEST — Open-clash density؛ RFI closure before work؛ shop-drawing completeness؛ access checks. 1 = >0% to <70% complete/closed OR multiple material open items/records are missing; closure/readiness is weak or poorly traceable. | INDICATOR TEST — Open-clash density؛ RFI closure before work؛ shop-drawing completeness؛ access checks. 0 = the required process/package/control is absent, a required critical action/test is not implemented, or a critical blocking item remains open. | N/A - non-critical indicator | Approved project specifications, ITP/WIR/NCR and construction infection/safety controls plus applicable AHJ requirements; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-CON-02 | Mandatory | Critical clashes per area/package؛ closure rate؛ model LOD/information completeness؛ sign-off responsibility. | BEP؛ federated model؛ clash reports؛ model issue log؛ approvals. | Process / completeness / readiness | INDICATOR TEST — Critical clashes per area/package؛ closure rate؛ model LOD/information completeness؛ sign-off responsibility. 4 = 100% of the required package, actions, records, tests, and approvals for the indicator are complete, current, traceable, and Verified; critical open items = 0. | INDICATOR TEST — Critical clashes per area/package؛ closure rate؛ model LOD/information completeness؛ sign-off responsibility. 3 = >=90% to <100% complete/closed; critical open items = 0; only minor administrative gaps remain and traceability/readiness is not materially impaired. | INDICATOR TEST — Critical clashes per area/package؛ closure rate؛ model LOD/information completeness؛ sign-off responsibility. 2 = >=70% to <90% complete/closed OR one material non-critical open item remains; the process is still auditable and a corrective path is defined. | INDICATOR TEST — Critical clashes per area/package؛ closure rate؛ model LOD/information completeness؛ sign-off responsibility. 1 = >0% to <70% complete/closed OR multiple material open items/records are missing; closure/readiness is weak or poorly traceable. | INDICATOR TEST — Critical clashes per area/package؛ closure rate؛ model LOD/information completeness؛ sign-off responsibility. 0 = the required process/package/control is absent, a required critical action/test is not implemented, or a critical blocking item remains open. | N/A - non-critical indicator | Approved project specifications, ITP/WIR/NCR and construction infection/safety controls plus applicable AHJ requirements; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-CON-03 | Critical Gate | نسبة الأعمال المخفية التي أغلقت بعد WIR/ITP مكتمل ونجاح الاختبارات المطلوبة. | ITP؛ WIR/MIR؛ photos؛ pressure/leak tests؛ firestop records. | Process / completeness / readiness | INDICATOR TEST — نسبة الأعمال المخفية التي أغلقت بعد WIR/ITP مكتمل ونجاح الاختبارات المطلوبة. 4 = 100% of the required package, actions, records, tests, and approvals for the indicator are complete, current, traceable, and Verified; critical open items = 0. | INDICATOR TEST — نسبة الأعمال المخفية التي أغلقت بعد WIR/ITP مكتمل ونجاح الاختبارات المطلوبة. 3 = >=90% to <100% complete/closed; critical open items = 0; only minor administrative gaps remain and traceability/readiness is not materially impaired. | INDICATOR TEST — نسبة الأعمال المخفية التي أغلقت بعد WIR/ITP مكتمل ونجاح الاختبارات المطلوبة. 2 = >=70% to <90% complete/closed OR one material non-critical open item remains; the process is still auditable and a corrective path is defined. | INDICATOR TEST — نسبة الأعمال المخفية التي أغلقت بعد WIR/ITP مكتمل ونجاح الاختبارات المطلوبة. 1 = >0% to <70% complete/closed OR multiple material open items/records are missing; closure/readiness is weak or poorly traceable. | INDICATOR TEST — نسبة الأعمال المخفية التي أغلقت بعد WIR/ITP مكتمل ونجاح الاختبارات المطلوبة. 0 = the required process/package/control is absent, a required critical action/test is not implemented, or a critical blocking item remains open. | INDICATOR GATE TEST — نسبة الأعمال المخفية التي أغلقت بعد WIR/ITP مكتمل ونجاح الاختبارات المطلوبة. PASS = Verified evidence demonstrates 100% completion and successful closure of all critical checklist/actions/tests in the indicator test; critical open items = 0. | Approved project specifications, ITP/WIR/NCR and construction infection/safety controls plus applicable AHJ requirements; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-CON-04 | Performance | First-pass yield؛ NCR rate؛ rework hours/cost؛ recurrence trend. | Inspection/test logs؛ NCR register؛ rework records؛ weekly quality trends. | Quantitative performance | INDICATOR TEST — First-pass yield؛ NCR rate؛ rework hours/cost؛ recurrence trend. 4 = 100% of the pre-locked required performance target(s) are met or exceeded under the required representative condition(s), with every mandatory minimum satisfied. | INDICATOR TEST — First-pass yield؛ NCR rate؛ rework hours/cost؛ recurrence trend. 3 = every mandatory minimum is satisfied and >=90% of the pre-locked performance targets are met; remaining variance is minor and non-critical. | INDICATOR TEST — First-pass yield؛ NCR rate؛ rework hours/cost؛ recurrence trend. 2 = >=75% to <90% of pre-locked performance targets are met, with material but correctable shortfall(s); no Verified failure of an essential mandatory minimum. | INDICATOR TEST — First-pass yield؛ NCR rate؛ rework hours/cost؛ recurrence trend. 1 = >0% to <75% of pre-locked performance targets are met OR repeated/large material shortfalls remain; performance is poorly controlled. | INDICATOR TEST — First-pass yield؛ NCR rate؛ rework hours/cost؛ recurrence trend. 0 = a Verified essential mandatory minimum fails, the required performance capability is absent, or none of the required target set is demonstrably achieved. | N/A - non-critical indicator | Approved project specifications, ITP/WIR/NCR and construction infection/safety controls plus applicable AHJ requirements; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-CON-05 | Critical Gate | Phase-specific access/ICRA/outage review؛ incident count؛ continuity test before each tie-in. | Phasing plan؛ ICRA؛ work permits؛ temporary services؛ tie-in/rollback plans. | Resilience / failure-scenario performance | INDICATOR TEST — Phase-specific access/ICRA/outage review؛ incident count؛ continuity test before each tie-in. 4 = 100% of the pre-defined normal, credible failure, maintenance, and recovery scenarios required for this indicator pass; critical function is maintained and the locked recovery target is met. | INDICATOR TEST — Phase-specific access/ICRA/outage review؛ incident count؛ continuity test before each tie-in. 3 = all critical functions and mandatory failover paths are maintained; only minor non-critical margin/timing variance (<=10% beyond the locked target) remains. | INDICATOR TEST — Phase-specific access/ICRA/outage review؛ incident count؛ continuity test before each tie-in. 2 = critical safety is maintained but one defined non-catastrophic resilience/failover scenario fails OR recovery is >10% to <=25% beyond the locked target; degraded service remains controlled. | INDICATOR TEST — Phase-specific access/ICRA/outage review؛ incident count؛ continuity test before each tie-in. 1 = critical resilience is materially weak, multiple scenarios fail, or recovery is >25% beyond the locked target; workaround/redundancy is not fully demonstrated. | INDICATOR TEST — Phase-specific access/ICRA/outage review؛ incident count؛ continuity test before each tie-in. 0 = a defined credible failure/outage causes loss of an essential critical function, unsafe state, or no credible failover/recovery path is demonstrated. | INDICATOR GATE TEST — Phase-specific access/ICRA/outage review؛ incident count؛ continuity test before each tie-in. PASS = Verified evidence demonstrates that all mandatory normal/failure/failover/recovery scenarios in the indicator test pass, essential critical function is maintained, and no unresolved critical failure remains. | Approved project specifications, ITP/WIR/NCR and construction infection/safety controls plus applicable AHJ requirements; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-CON-06 | Mandatory | Document completeness index + open critical defects + retest closure. | ITP؛ WIR/MIR؛ test reports؛ NCRs؛ punch list؛ retest evidence. | Process / completeness / readiness | INDICATOR TEST — Document completeness index + open critical defects + retest closure. 4 = 100% of the required package, actions, records, tests, and approvals for the indicator are complete, current, traceable, and Verified; critical open items = 0. | INDICATOR TEST — Document completeness index + open critical defects + retest closure. 3 = >=90% to <100% complete/closed; critical open items = 0; only minor administrative gaps remain and traceability/readiness is not materially impaired. | INDICATOR TEST — Document completeness index + open critical defects + retest closure. 2 = >=70% to <90% complete/closed OR one material non-critical open item remains; the process is still auditable and a corrective path is defined. | INDICATOR TEST — Document completeness index + open critical defects + retest closure. 1 = >0% to <70% complete/closed OR multiple material open items/records are missing; closure/readiness is weak or poorly traceable. | INDICATOR TEST — Document completeness index + open critical defects + retest closure. 0 = the required process/package/control is absent, a required critical action/test is not implemented, or a critical blocking item remains open. | N/A - non-critical indicator | Approved project specifications, ITP/WIR/NCR and construction infection/safety controls plus applicable AHJ requirements; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-COM-01 | Mandatory | Commissioning completion + functional performance tests + unresolved deficiency count. | Commissioning plan/reports؛ TAB؛ functional tests؛ deficiency log. | Process / completeness / readiness | INDICATOR TEST — Commissioning completion + functional performance tests + unresolved deficiency count. 4 = 100% of the required package, actions, records, tests, and approvals for the indicator are complete, current, traceable, and Verified; critical open items = 0. | INDICATOR TEST — Commissioning completion + functional performance tests + unresolved deficiency count. 3 = >=90% to <100% complete/closed; critical open items = 0; only minor administrative gaps remain and traceability/readiness is not materially impaired. | INDICATOR TEST — Commissioning completion + functional performance tests + unresolved deficiency count. 2 = >=70% to <90% complete/closed OR one material non-critical open item remains; the process is still auditable and a corrective path is defined. | INDICATOR TEST — Commissioning completion + functional performance tests + unresolved deficiency count. 1 = >0% to <70% complete/closed OR multiple material open items/records are missing; closure/readiness is weak or poorly traceable. | INDICATOR TEST — Commissioning completion + functional performance tests + unresolved deficiency count. 0 = the required process/package/control is absent, a required critical action/test is not implemented, or a critical blocking item remains open. | N/A - non-critical indicator | Approved commissioning plan, functional-performance/integrated-system testing acceptance criteria and project specifications; CBAHI readiness requirements; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-COM-02 | Critical Gate | IST scenario pass rate؛ interface failures؛ timing deviations؛ corrective retest. | IST scripts؛ cause/effect؛ timestamps؛ integrated test reports. | Resilience / failure-scenario performance | INDICATOR TEST — IST scenario pass rate؛ interface failures؛ timing deviations؛ corrective retest. 4 = 100% of the pre-defined normal, credible failure, maintenance, and recovery scenarios required for this indicator pass; critical function is maintained and the locked recovery target is met. | INDICATOR TEST — IST scenario pass rate؛ interface failures؛ timing deviations؛ corrective retest. 3 = all critical functions and mandatory failover paths are maintained; only minor non-critical margin/timing variance (<=10% beyond the locked target) remains. | INDICATOR TEST — IST scenario pass rate؛ interface failures؛ timing deviations؛ corrective retest. 2 = critical safety is maintained but one defined non-catastrophic resilience/failover scenario fails OR recovery is >10% to <=25% beyond the locked target; degraded service remains controlled. | INDICATOR TEST — IST scenario pass rate؛ interface failures؛ timing deviations؛ corrective retest. 1 = critical resilience is materially weak, multiple scenarios fail, or recovery is >25% beyond the locked target; workaround/redundancy is not fully demonstrated. | INDICATOR TEST — IST scenario pass rate؛ interface failures؛ timing deviations؛ corrective retest. 0 = a defined credible failure/outage causes loss of an essential critical function, unsafe state, or no credible failover/recovery path is demonstrated. | INDICATOR GATE TEST — IST scenario pass rate؛ interface failures؛ timing deviations؛ corrective retest. PASS = Verified evidence demonstrates that all mandatory normal/failure/failover/recovery scenarios in the indicator test pass, essential critical function is maintained, and no unresolved critical failure remains. | Approved commissioning plan, functional-performance/integrated-system testing acceptance criteria and project specifications; CBAHI readiness requirements; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-OPS-01 | Mandatory | Readiness index across work/records/training/spares/permits/transition with critical-open-item stop. | Readiness checklist؛ training records؛ permits؛ spare-parts list؛ transition plan. | Process / completeness / readiness | INDICATOR TEST — Readiness index across work/records/training/spares/permits/transition with critical-open-item stop. 4 = 100% of the required package, actions, records, tests, and approvals for the indicator are complete, current, traceable, and Verified; critical open items = 0. | INDICATOR TEST — Readiness index across work/records/training/spares/permits/transition with critical-open-item stop. 3 = >=90% to <100% complete/closed; critical open items = 0; only minor administrative gaps remain and traceability/readiness is not materially impaired. | INDICATOR TEST — Readiness index across work/records/training/spares/permits/transition with critical-open-item stop. 2 = >=70% to <90% complete/closed OR one material non-critical open item remains; the process is still auditable and a corrective path is defined. | INDICATOR TEST — Readiness index across work/records/training/spares/permits/transition with critical-open-item stop. 1 = >0% to <70% complete/closed OR multiple material open items/records are missing; closure/readiness is weak or poorly traceable. | INDICATOR TEST — Readiness index across work/records/training/spares/permits/transition with critical-open-item stop. 0 = the required process/package/control is absent, a required critical action/test is not implemented, or a critical blocking item remains open. | N/A - non-critical indicator | Approved operational-readiness, facility SLA and asset-handover requirements; CBAHI Hospital Standards; WELL Health-Safety Rating Guidebook Q2 2021 as operational/documentation benchmark; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-OPS-02 | Mandatory | نسبة الأصول الحرجة ذات بيانات كاملة ومربوطة بـBIM/COBie/CMMS وO&M وضمانات وقطع غيار. | Asset register؛ BIM/COBie؛ CMMS upload؛ O&M manuals؛ warranties. | Process / completeness / readiness | INDICATOR TEST — نسبة الأصول الحرجة ذات بيانات كاملة ومربوطة بـBIM/COBie/CMMS وO&M وضمانات وقطع غيار. 4 = 100% of the required package, actions, records, tests, and approvals for the indicator are complete, current, traceable, and Verified; critical open items = 0. | INDICATOR TEST — نسبة الأصول الحرجة ذات بيانات كاملة ومربوطة بـBIM/COBie/CMMS وO&M وضمانات وقطع غيار. 3 = >=90% to <100% complete/closed; critical open items = 0; only minor administrative gaps remain and traceability/readiness is not materially impaired. | INDICATOR TEST — نسبة الأصول الحرجة ذات بيانات كاملة ومربوطة بـBIM/COBie/CMMS وO&M وضمانات وقطع غيار. 2 = >=70% to <90% complete/closed OR one material non-critical open item remains; the process is still auditable and a corrective path is defined. | INDICATOR TEST — نسبة الأصول الحرجة ذات بيانات كاملة ومربوطة بـBIM/COBie/CMMS وO&M وضمانات وقطع غيار. 1 = >0% to <70% complete/closed OR multiple material open items/records are missing; closure/readiness is weak or poorly traceable. | INDICATOR TEST — نسبة الأصول الحرجة ذات بيانات كاملة ومربوطة بـBIM/COBie/CMMS وO&M وضمانات وقطع غيار. 0 = the required process/package/control is absent, a required critical action/test is not implemented, or a critical blocking item remains open. | N/A - non-critical indicator | Approved operational-readiness, facility SLA and asset-handover requirements; CBAHI Hospital Standards; WELL Health-Safety Rating Guidebook Q2 2021 as operational/documentation benchmark; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-OPS-03 | Performance | Occupancy/use density by time period؛ peak queue/load versus design assumptions. | Scheduling/appointment data؛ sensor counts؛ elevator logs؛ space observations. | Quantitative performance | INDICATOR TEST — Occupancy/use density by time period؛ peak queue/load versus design assumptions. 4 = 100% of the pre-locked required performance target(s) are met or exceeded under the required representative condition(s), with every mandatory minimum satisfied. | INDICATOR TEST — Occupancy/use density by time period؛ peak queue/load versus design assumptions. 3 = every mandatory minimum is satisfied and >=90% of the pre-locked performance targets are met; remaining variance is minor and non-critical. | INDICATOR TEST — Occupancy/use density by time period؛ peak queue/load versus design assumptions. 2 = >=75% to <90% of pre-locked performance targets are met, with material but correctable shortfall(s); no Verified failure of an essential mandatory minimum. | INDICATOR TEST — Occupancy/use density by time period؛ peak queue/load versus design assumptions. 1 = >0% to <75% of pre-locked performance targets are met OR repeated/large material shortfalls remain; performance is poorly controlled. | INDICATOR TEST — Occupancy/use density by time period؛ peak queue/load versus design assumptions. 0 = a Verified essential mandatory minimum fails, the required performance capability is absent, or none of the required target set is demonstrably achieved. | N/A - non-critical indicator | Approved operational-readiness, facility SLA and asset-handover requirements; CBAHI Hospital Standards; WELL Health-Safety Rating Guidebook Q2 2021 as operational/documentation benchmark; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-LIF-01 | Mandatory | Maintenance-access audit؛ isolation test؛ mean repair time؛ unsafe/inaccessible asset count. | Maintenance clearances؛ isolation diagrams؛ CMMS work orders؛ field audit. | Operational / lifecycle performance | INDICATOR TEST — Maintenance-access audit؛ isolation test؛ mean repair time؛ unsafe/inaccessible asset count. 4 = >=95% of the pre-locked operational/lifecycle targets are met across the defined observation period; critical backlog, unsafe assets, and uncontained critical exceptions = 0. | INDICATOR TEST — Maintenance-access audit؛ isolation test؛ mean repair time؛ unsafe/inaccessible asset count. 3 = >=90% to <95% of targets are met; no critical service impact or uncontained critical backlog exists; only minor isolated variance remains. | INDICATOR TEST — Maintenance-access audit؛ isolation test؛ mean repair time؛ unsafe/inaccessible asset count. 2 = >=75% to <90% of targets are met OR recurring moderate gaps exist with controlled impact and a documented corrective plan. | INDICATOR TEST — Maintenance-access audit؛ isolation test؛ mean repair time؛ unsafe/inaccessible asset count. 1 = >=50% to <75% of targets are met OR recurrent major gaps/overdue material actions materially affect maintainability, reliability, data quality, or operations. | INDICATOR TEST — Maintenance-access audit؛ isolation test؛ mean repair time؛ unsafe/inaccessible asset count. 0 = <50% of targets are met, or a critical operational capability/control is failed, unsafe, unavailable, or not effectively controlled. | N/A - non-critical indicator | Approved FM/maintenance/POE SLA, asset-management and lifecycle policies; CBAHI Hospital Standards; WELL Health-Safety Rating Guidebook Q2 2021; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-LIF-02 | Mandatory | Route clearance / turning / floor-load check + replacement scenario walkthrough. | Replacement-route drawings؛ lifting plan؛ equipment dimensions؛ floor-load data. | Operational / lifecycle performance | INDICATOR TEST — Route clearance / turning / floor-load check + replacement scenario walkthrough. 4 = >=95% of the pre-locked operational/lifecycle targets are met across the defined observation period; critical backlog, unsafe assets, and uncontained critical exceptions = 0. | INDICATOR TEST — Route clearance / turning / floor-load check + replacement scenario walkthrough. 3 = >=90% to <95% of targets are met; no critical service impact or uncontained critical backlog exists; only minor isolated variance remains. | INDICATOR TEST — Route clearance / turning / floor-load check + replacement scenario walkthrough. 2 = >=75% to <90% of targets are met OR recurring moderate gaps exist with controlled impact and a documented corrective plan. | INDICATOR TEST — Route clearance / turning / floor-load check + replacement scenario walkthrough. 1 = >=50% to <75% of targets are met OR recurrent major gaps/overdue material actions materially affect maintainability, reliability, data quality, or operations. | INDICATOR TEST — Route clearance / turning / floor-load check + replacement scenario walkthrough. 0 = <50% of targets are met, or a critical operational capability/control is failed, unsafe, unavailable, or not effectively controlled. | N/A - non-critical indicator | Approved FM/maintenance/POE SLA, asset-management and lifecycle policies; CBAHI Hospital Standards; WELL Health-Safety Rating Guidebook Q2 2021; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-LIF-03 | Mandatory | Critical-spare fill rate؛ lead time؛ stock-out incidents؛ risk-based spare list coverage. | Spare-parts register؛ supplier lead times؛ CMMS inventory؛ criticality analysis. | Operational / lifecycle performance | INDICATOR TEST — Critical-spare fill rate؛ lead time؛ stock-out incidents؛ risk-based spare list coverage. 4 = >=95% of the pre-locked operational/lifecycle targets are met across the defined observation period; critical backlog, unsafe assets, and uncontained critical exceptions = 0. | INDICATOR TEST — Critical-spare fill rate؛ lead time؛ stock-out incidents؛ risk-based spare list coverage. 3 = >=90% to <95% of targets are met; no critical service impact or uncontained critical backlog exists; only minor isolated variance remains. | INDICATOR TEST — Critical-spare fill rate؛ lead time؛ stock-out incidents؛ risk-based spare list coverage. 2 = >=75% to <90% of targets are met OR recurring moderate gaps exist with controlled impact and a documented corrective plan. | INDICATOR TEST — Critical-spare fill rate؛ lead time؛ stock-out incidents؛ risk-based spare list coverage. 1 = >=50% to <75% of targets are met OR recurrent major gaps/overdue material actions materially affect maintainability, reliability, data quality, or operations. | INDICATOR TEST — Critical-spare fill rate؛ lead time؛ stock-out incidents؛ risk-based spare list coverage. 0 = <50% of targets are met, or a critical operational capability/control is failed, unsafe, unavailable, or not effectively controlled. | N/A - non-critical indicator | Approved FM/maintenance/POE SLA, asset-management and lifecycle policies; CBAHI Hospital Standards; WELL Health-Safety Rating Guidebook Q2 2021; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-LIF-04 | Mandatory | Skill coverage per shift؛ response-time test؛ competency/training completion. | Roster؛ competency matrix؛ training records؛ call-out logs. | Operational / lifecycle performance | INDICATOR TEST — Skill coverage per shift؛ response-time test؛ competency/training completion. 4 = >=95% of the pre-locked operational/lifecycle targets are met across the defined observation period; critical backlog, unsafe assets, and uncontained critical exceptions = 0. | INDICATOR TEST — Skill coverage per shift؛ response-time test؛ competency/training completion. 3 = >=90% to <95% of targets are met; no critical service impact or uncontained critical backlog exists; only minor isolated variance remains. | INDICATOR TEST — Skill coverage per shift؛ response-time test؛ competency/training completion. 2 = >=75% to <90% of targets are met OR recurring moderate gaps exist with controlled impact and a documented corrective plan. | INDICATOR TEST — Skill coverage per shift؛ response-time test؛ competency/training completion. 1 = >=50% to <75% of targets are met OR recurrent major gaps/overdue material actions materially affect maintainability, reliability, data quality, or operations. | INDICATOR TEST — Skill coverage per shift؛ response-time test؛ competency/training completion. 0 = <50% of targets are met, or a critical operational capability/control is failed, unsafe, unavailable, or not effectively controlled. | N/A - non-critical indicator | Approved FM/maintenance/POE SLA, asset-management and lifecycle policies; CBAHI Hospital Standards; WELL Health-Safety Rating Guidebook Q2 2021; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-LIF-05 | Performance | Response time؛ MTTR؛ recurrence rate؛ backlog age by criticality. | CMMS work orders؛ fault logs؛ escalation records. | Quantitative performance | INDICATOR TEST — Response time؛ MTTR؛ recurrence rate؛ backlog age by criticality. 4 = 100% of the pre-locked required performance target(s) are met or exceeded under the required representative condition(s), with every mandatory minimum satisfied. | INDICATOR TEST — Response time؛ MTTR؛ recurrence rate؛ backlog age by criticality. 3 = every mandatory minimum is satisfied and >=90% of the pre-locked performance targets are met; remaining variance is minor and non-critical. | INDICATOR TEST — Response time؛ MTTR؛ recurrence rate؛ backlog age by criticality. 2 = >=75% to <90% of pre-locked performance targets are met, with material but correctable shortfall(s); no Verified failure of an essential mandatory minimum. | INDICATOR TEST — Response time؛ MTTR؛ recurrence rate؛ backlog age by criticality. 1 = >0% to <75% of pre-locked performance targets are met OR repeated/large material shortfalls remain; performance is poorly controlled. | INDICATOR TEST — Response time؛ MTTR؛ recurrence rate؛ backlog age by criticality. 0 = a Verified essential mandatory minimum fails, the required performance capability is absent, or none of the required target set is demonstrably achieved. | N/A - non-critical indicator | Approved FM/maintenance/POE SLA, asset-management and lifecycle policies; CBAHI Hospital Standards; WELL Health-Safety Rating Guidebook Q2 2021; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-LIF-06 | Performance | Scenario test for renewal without full shutdown؛ affected clinical area/time; rollback readiness. | Renewal strategy؛ isolation plan؛ temporary-services plan؛ phasing drawings. | Resilience / failure-scenario performance | INDICATOR TEST — Scenario test for renewal without full shutdown؛ affected clinical area/time; rollback readiness. 4 = 100% of the pre-defined normal, credible failure, maintenance, and recovery scenarios required for this indicator pass; critical function is maintained and the locked recovery target is met. | INDICATOR TEST — Scenario test for renewal without full shutdown؛ affected clinical area/time; rollback readiness. 3 = all critical functions and mandatory failover paths are maintained; only minor non-critical margin/timing variance (<=10% beyond the locked target) remains. | INDICATOR TEST — Scenario test for renewal without full shutdown؛ affected clinical area/time; rollback readiness. 2 = critical safety is maintained but one defined non-catastrophic resilience/failover scenario fails OR recovery is >10% to <=25% beyond the locked target; degraded service remains controlled. | INDICATOR TEST — Scenario test for renewal without full shutdown؛ affected clinical area/time; rollback readiness. 1 = critical resilience is materially weak, multiple scenarios fail, or recovery is >25% beyond the locked target; workaround/redundancy is not fully demonstrated. | INDICATOR TEST — Scenario test for renewal without full shutdown؛ affected clinical area/time; rollback readiness. 0 = a defined credible failure/outage causes loss of an essential critical function, unsafe state, or no credible failover/recovery path is demonstrated. | N/A - non-critical indicator | Approved FM/maintenance/POE SLA, asset-management and lifecycle policies; CBAHI Hospital Standards; WELL Health-Safety Rating Guidebook Q2 2021; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-LIF-07 | Performance | Condition score؛ critical defects؛ closure time؛ repeat defect rate. | Condition surveys؛ defect register؛ fire/infection barrier inspection records. | Operational / lifecycle performance | INDICATOR TEST — Condition score؛ critical defects؛ closure time؛ repeat defect rate. 4 = >=95% of the pre-locked operational/lifecycle targets are met across the defined observation period; critical backlog, unsafe assets, and uncontained critical exceptions = 0. | INDICATOR TEST — Condition score؛ critical defects؛ closure time؛ repeat defect rate. 3 = >=90% to <95% of targets are met; no critical service impact or uncontained critical backlog exists; only minor isolated variance remains. | INDICATOR TEST — Condition score؛ critical defects؛ closure time؛ repeat defect rate. 2 = >=75% to <90% of targets are met OR recurring moderate gaps exist with controlled impact and a documented corrective plan. | INDICATOR TEST — Condition score؛ critical defects؛ closure time؛ repeat defect rate. 1 = >=50% to <75% of targets are met OR recurrent major gaps/overdue material actions materially affect maintainability, reliability, data quality, or operations. | INDICATOR TEST — Condition score؛ critical defects؛ closure time؛ repeat defect rate. 0 = <50% of targets are met, or a critical operational capability/control is failed, unsafe, unavailable, or not effectively controlled. | N/A - non-critical indicator | Approved FM/maintenance/POE SLA, asset-management and lifecycle policies; CBAHI Hospital Standards; WELL Health-Safety Rating Guidebook Q2 2021; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-LIF-08 | Mandatory | POE at defined post-occupancy interval؛ comparison of measured outcomes to design assumptions. | POE report؛ user surveys؛ CMMS/BMS؛ movement/queue data؛ complaints. | Operational / lifecycle performance | INDICATOR TEST — POE at defined post-occupancy interval؛ comparison of measured outcomes to design assumptions. 4 = >=95% of the pre-locked operational/lifecycle targets are met across the defined observation period; critical backlog, unsafe assets, and uncontained critical exceptions = 0. | INDICATOR TEST — POE at defined post-occupancy interval؛ comparison of measured outcomes to design assumptions. 3 = >=90% to <95% of targets are met; no critical service impact or uncontained critical backlog exists; only minor isolated variance remains. | INDICATOR TEST — POE at defined post-occupancy interval؛ comparison of measured outcomes to design assumptions. 2 = >=75% to <90% of targets are met OR recurring moderate gaps exist with controlled impact and a documented corrective plan. | INDICATOR TEST — POE at defined post-occupancy interval؛ comparison of measured outcomes to design assumptions. 1 = >=50% to <75% of targets are met OR recurrent major gaps/overdue material actions materially affect maintainability, reliability, data quality, or operations. | INDICATOR TEST — POE at defined post-occupancy interval؛ comparison of measured outcomes to design assumptions. 0 = <50% of targets are met, or a critical operational capability/control is failed, unsafe, unavailable, or not effectively controlled. | N/A - non-critical indicator | Approved FM/maintenance/POE SLA, asset-management and lifecycle policies; CBAHI Hospital Standards; WELL Health-Safety Rating Guidebook Q2 2021; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-LIF-09 | Performance | Number/severity of gaps؛ closure rate/time؛ post-correction verification. | POE findings؛ corrective-action register؛ revised SOP/design records؛ follow-up data. | Operational / lifecycle performance | INDICATOR TEST — Number/severity of gaps؛ closure rate/time؛ post-correction verification. 4 = >=95% of the pre-locked operational/lifecycle targets are met across the defined observation period; critical backlog, unsafe assets, and uncontained critical exceptions = 0. | INDICATOR TEST — Number/severity of gaps؛ closure rate/time؛ post-correction verification. 3 = >=90% to <95% of targets are met; no critical service impact or uncontained critical backlog exists; only minor isolated variance remains. | INDICATOR TEST — Number/severity of gaps؛ closure rate/time؛ post-correction verification. 2 = >=75% to <90% of targets are met OR recurring moderate gaps exist with controlled impact and a documented corrective plan. | INDICATOR TEST — Number/severity of gaps؛ closure rate/time؛ post-correction verification. 1 = >=50% to <75% of targets are met OR recurrent major gaps/overdue material actions materially affect maintainability, reliability, data quality, or operations. | INDICATOR TEST — Number/severity of gaps؛ closure rate/time؛ post-correction verification. 0 = <50% of targets are met, or a critical operational capability/control is failed, unsafe, unavailable, or not effectively controlled. | N/A - non-critical indicator | Approved FM/maintenance/POE SLA, asset-management and lifecycle policies; CBAHI Hospital Standards; WELL Health-Safety Rating Guidebook Q2 2021; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-LIF-10 | Performance | LCC/NPV comparison over declared study period + sensitivity of key assumptions. | LCC model؛ capex/opex assumptions؛ maintenance/replacement schedules. | Economic / option appraisal | INDICATOR TEST — LCC/NPV comparison over declared study period + sensitivity of key assumptions. 4 = 100% of required alternatives, life-cycle cost/NPV inputs, assumptions, risks, uncertainty/sensitivity tests, and decision trace are complete, transparent, and auditable. | INDICATOR TEST — LCC/NPV comparison over declared study period + sensitivity of key assumptions. 3 = the core comparison is complete and >=90% of required inputs/assumptions are documented; minor omissions do not change the decision basis. | INDICATOR TEST — LCC/NPV comparison over declared study period + sensitivity of key assumptions. 2 = >=70% to <90% of required appraisal elements are complete OR one material risk/sensitivity/assumption gap remains; the decision is still interpretable. | INDICATOR TEST — LCC/NPV comparison over declared study period + sensitivity of key assumptions. 1 = >0% to <70% of required appraisal elements are complete OR major cost/risk/alternative assumptions are missing; decision support is weak. | INDICATOR TEST — LCC/NPV comparison over declared study period + sensitivity of key assumptions. 0 = no credible auditable comparison exists, required alternatives are not evaluated, or the decision is unsupported by traceable analysis. | N/A - non-critical indicator | Approved FM/maintenance/POE SLA, asset-management and lifecycle policies; CBAHI Hospital Standards; WELL Health-Safety Rating Guidebook Q2 2021; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); CBAHI Hospital Standards — exact project-adopted edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-DIG-01 | Mandatory | Completeness/validity/timestamp coverage؛ asset-ID match rate؛ missing/invalid data rate. | Point list؛ BMS trends؛ CMMS asset/work-order data؛ data-quality audit. | Operational / lifecycle performance | INDICATOR TEST — Completeness/validity/timestamp coverage؛ asset-ID match rate؛ missing/invalid data rate. 4 = >=95% of the pre-locked operational/lifecycle targets are met across the defined observation period; critical backlog, unsafe assets, and uncontained critical exceptions = 0. | INDICATOR TEST — Completeness/validity/timestamp coverage؛ asset-ID match rate؛ missing/invalid data rate. 3 = >=90% to <95% of targets are met; no critical service impact or uncontained critical backlog exists; only minor isolated variance remains. | INDICATOR TEST — Completeness/validity/timestamp coverage؛ asset-ID match rate؛ missing/invalid data rate. 2 = >=75% to <90% of targets are met OR recurring moderate gaps exist with controlled impact and a documented corrective plan. | INDICATOR TEST — Completeness/validity/timestamp coverage؛ asset-ID match rate؛ missing/invalid data rate. 1 = >=50% to <75% of targets are met OR recurrent major gaps/overdue material actions materially affect maintainability, reliability, data quality, or operations. | INDICATOR TEST — Completeness/validity/timestamp coverage؛ asset-ID match rate؛ missing/invalid data rate. 0 = <50% of targets are met, or a critical operational capability/control is failed, unsafe, unavailable, or not effectively controlled. | N/A - non-critical indicator | Approved BIM/COBie/CMMS/BMS information requirements, model/data validation plan and operational data governance; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-DIG-02 | Performance | Alarm rate per asset/time؛ nuisance-alarm share؛ acknowledgement/response time. | Alarm history؛ rationalization register؛ response logs. | Quantitative performance | INDICATOR TEST — Alarm rate per asset/time؛ nuisance-alarm share؛ acknowledgement/response time. 4 = 100% of the pre-locked required performance target(s) are met or exceeded under the required representative condition(s), with every mandatory minimum satisfied. | INDICATOR TEST — Alarm rate per asset/time؛ nuisance-alarm share؛ acknowledgement/response time. 3 = every mandatory minimum is satisfied and >=90% of the pre-locked performance targets are met; remaining variance is minor and non-critical. | INDICATOR TEST — Alarm rate per asset/time؛ nuisance-alarm share؛ acknowledgement/response time. 2 = >=75% to <90% of pre-locked performance targets are met, with material but correctable shortfall(s); no Verified failure of an essential mandatory minimum. | INDICATOR TEST — Alarm rate per asset/time؛ nuisance-alarm share؛ acknowledgement/response time. 1 = >0% to <75% of pre-locked performance targets are met OR repeated/large material shortfalls remain; performance is poorly controlled. | INDICATOR TEST — Alarm rate per asset/time؛ nuisance-alarm share؛ acknowledgement/response time. 0 = a Verified essential mandatory minimum fails, the required performance capability is absent, or none of the required target set is demonstrably achieved. | N/A - non-critical indicator | Approved BIM/COBie/CMMS/BMS information requirements, model/data validation plan and operational data governance; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-DIG-03 | Enhancement | Trend anomaly detection with confirmed maintenance findings / avoided failures. | Trend analytics؛ predictive-maintenance records؛ condition-monitoring data. | Operational / lifecycle performance | INDICATOR TEST — Trend anomaly detection with confirmed maintenance findings / avoided failures. 4 = >=95% of the pre-locked operational/lifecycle targets are met across the defined observation period; critical backlog, unsafe assets, and uncontained critical exceptions = 0. | INDICATOR TEST — Trend anomaly detection with confirmed maintenance findings / avoided failures. 3 = >=90% to <95% of targets are met; no critical service impact or uncontained critical backlog exists; only minor isolated variance remains. | INDICATOR TEST — Trend anomaly detection with confirmed maintenance findings / avoided failures. 2 = >=75% to <90% of targets are met OR recurring moderate gaps exist with controlled impact and a documented corrective plan. | INDICATOR TEST — Trend anomaly detection with confirmed maintenance findings / avoided failures. 1 = >=50% to <75% of targets are met OR recurrent major gaps/overdue material actions materially affect maintainability, reliability, data quality, or operations. | INDICATOR TEST — Trend anomaly detection with confirmed maintenance findings / avoided failures. 0 = <50% of targets are met, or a critical operational capability/control is failed, unsafe, unavailable, or not effectively controlled. | N/A - non-critical indicator | Approved BIM/COBie/CMMS/BMS information requirements, model/data validation plan and operational data governance; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-DIG-04 | Mandatory | LOD/LOI completeness by required use; data-field completion; approved model exchanges. | BEP؛ federated model؛ model audit؛ COBie/asset data. | Operational / lifecycle performance | INDICATOR TEST — LOD/LOI completeness by required use; data-field completion; approved model exchanges. 4 = >=95% of the pre-locked operational/lifecycle targets are met across the defined observation period; critical backlog, unsafe assets, and uncontained critical exceptions = 0. | INDICATOR TEST — LOD/LOI completeness by required use; data-field completion; approved model exchanges. 3 = >=90% to <95% of targets are met; no critical service impact or uncontained critical backlog exists; only minor isolated variance remains. | INDICATOR TEST — LOD/LOI completeness by required use; data-field completion; approved model exchanges. 2 = >=75% to <90% of targets are met OR recurring moderate gaps exist with controlled impact and a documented corrective plan. | INDICATOR TEST — LOD/LOI completeness by required use; data-field completion; approved model exchanges. 1 = >=50% to <75% of targets are met OR recurrent major gaps/overdue material actions materially affect maintainability, reliability, data quality, or operations. | INDICATOR TEST — LOD/LOI completeness by required use; data-field completion; approved model exchanges. 0 = <50% of targets are met, or a critical operational capability/control is failed, unsafe, unavailable, or not effectively controlled. | N/A - non-critical indicator | Approved BIM/COBie/CMMS/BMS information requirements, model/data validation plan and operational data governance; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-DIG-05 | Mandatory | Audit trace from input → model/version → calculation/output → reviewer/sign-off. | Calculation reports؛ model version history؛ assumptions register؛ professional sign-off. | Operational / lifecycle performance | INDICATOR TEST — Audit trace from input → model/version → calculation/output → reviewer/sign-off. 4 = >=95% of the pre-locked operational/lifecycle targets are met across the defined observation period; critical backlog, unsafe assets, and uncontained critical exceptions = 0. | INDICATOR TEST — Audit trace from input → model/version → calculation/output → reviewer/sign-off. 3 = >=90% to <95% of targets are met; no critical service impact or uncontained critical backlog exists; only minor isolated variance remains. | INDICATOR TEST — Audit trace from input → model/version → calculation/output → reviewer/sign-off. 2 = >=75% to <90% of targets are met OR recurring moderate gaps exist with controlled impact and a documented corrective plan. | INDICATOR TEST — Audit trace from input → model/version → calculation/output → reviewer/sign-off. 1 = >=50% to <75% of targets are met OR recurrent major gaps/overdue material actions materially affect maintainability, reliability, data quality, or operations. | INDICATOR TEST — Audit trace from input → model/version → calculation/output → reviewer/sign-off. 0 = <50% of targets are met, or a critical operational capability/control is failed, unsafe, unavailable, or not effectively controlled. | N/A - non-critical indicator | Approved BIM/COBie/CMMS/BMS information requirements, model/data validation plan and operational data governance; HRWHPI V2.1 frozen set. | CR-01 v1.0 (2026-08-10); Applicable project/AHJ source edition/clause to be logged. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-GOV-01 | Critical Gate | Pass/Fail/Conditional gate review at each stage + closure evidence before progression. | Gate register؛ review minutes؛ risk/issue closure؛ approvals. | Regulatory / gate compliance | INDICATOR TEST — Pass/Fail/Conditional gate review at each stage + closure evidence before progression. 4 = 100% of applicable essential/mandatory requirements for the indicator test are Verified as satisfied; required approvals/acceptances are current; no material, blocking, or unapproved exception remains. | INDICATOR TEST — Pass/Fail/Conditional gate review at each stage + closure evidence before progression. 3 = all essential/mandatory requirements are satisfied and >=90% of non-critical checklist/record elements are complete; only minor non-material gaps remain; no acceptance-blocking item. | INDICATOR TEST — Pass/Fail/Conditional gate review at each stage + closure evidence before progression. 2 = 70% to <90% of non-critical checklist/record elements are complete OR one material but correctable gap remains; no Verified failure of an essential mandatory requirement. | INDICATOR TEST — Pass/Fail/Conditional gate review at each stage + closure evidence before progression. 1 = >0% to <70% of required elements are complete/satisfied OR multiple material gaps/open approvals remain; the compliance/control is substantially deficient. | INDICATOR TEST — Pass/Fail/Conditional gate review at each stage + closure evidence before progression. 0 = Verified failure/non-compliance of an essential mandatory requirement, rejected/absent required approval, prohibited condition, or required control is absent. | INDICATOR GATE TEST — Pass/Fail/Conditional gate review at each stage + closure evidence before progression. PASS = Verified evidence demonstrates 100% satisfaction of all applicable essential mandatory requirements/approvals in the indicator test, with no blocking item, rejected requirement, or unapproved exception. | HRWHPI governance/evidence protocol; IFC Performance Standards effective 2012 PS1 as risk-management benchmark; WELL Health-Safety Rating Guidebook Q2 2021 as documentation/governance benchmark. | CR-01 v1.0 (2026-08-10); IFC PS (effective 2012) PS1 benchmark; WELL Health-Safety Guidebook Q2 2021 benchmark. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-GOV-02 | Mandatory | نسبة التغييرات ذات impact assessment مكتمل وموافقة قبل التنفيذ؛ critical-change exceptions. | Change log؛ impact assessment؛ updated BIM/drawings؛ approvals؛ risk update. | Process / completeness / readiness | INDICATOR TEST — نسبة التغييرات ذات impact assessment مكتمل وموافقة قبل التنفيذ؛ critical-change exceptions. 4 = 100% of the required package, actions, records, tests, and approvals for the indicator are complete, current, traceable, and Verified; critical open items = 0. | INDICATOR TEST — نسبة التغييرات ذات impact assessment مكتمل وموافقة قبل التنفيذ؛ critical-change exceptions. 3 = >=90% to <100% complete/closed; critical open items = 0; only minor administrative gaps remain and traceability/readiness is not materially impaired. | INDICATOR TEST — نسبة التغييرات ذات impact assessment مكتمل وموافقة قبل التنفيذ؛ critical-change exceptions. 2 = >=70% to <90% complete/closed OR one material non-critical open item remains; the process is still auditable and a corrective path is defined. | INDICATOR TEST — نسبة التغييرات ذات impact assessment مكتمل وموافقة قبل التنفيذ؛ critical-change exceptions. 1 = >0% to <70% complete/closed OR multiple material open items/records are missing; closure/readiness is weak or poorly traceable. | INDICATOR TEST — نسبة التغييرات ذات impact assessment مكتمل وموافقة قبل التنفيذ؛ critical-change exceptions. 0 = the required process/package/control is absent, a required critical action/test is not implemented, or a critical blocking item remains open. | N/A - non-critical indicator | HRWHPI governance/evidence protocol; IFC Performance Standards effective 2012 PS1 as risk-management benchmark; WELL Health-Safety Rating Guidebook Q2 2021 as documentation/governance benchmark. | CR-01 v1.0 (2026-08-10); IFC PS (effective 2012) PS1 benchmark; WELL Health-Safety Guidebook Q2 2021 benchmark. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-GOV-03 | Mandatory | Completeness of option appraisal; sensitivity/assumption documentation; decision trace. | Option appraisal؛ risk register؛ simulation/LCC outputs؛ user comments؛ approval minutes. | Process / completeness / readiness | INDICATOR TEST — Completeness of option appraisal; sensitivity/assumption documentation; decision trace. 4 = 100% of the required package, actions, records, tests, and approvals for the indicator are complete, current, traceable, and Verified; critical open items = 0. | INDICATOR TEST — Completeness of option appraisal; sensitivity/assumption documentation; decision trace. 3 = >=90% to <100% complete/closed; critical open items = 0; only minor administrative gaps remain and traceability/readiness is not materially impaired. | INDICATOR TEST — Completeness of option appraisal; sensitivity/assumption documentation; decision trace. 2 = >=70% to <90% complete/closed OR one material non-critical open item remains; the process is still auditable and a corrective path is defined. | INDICATOR TEST — Completeness of option appraisal; sensitivity/assumption documentation; decision trace. 1 = >0% to <70% complete/closed OR multiple material open items/records are missing; closure/readiness is weak or poorly traceable. | INDICATOR TEST — Completeness of option appraisal; sensitivity/assumption documentation; decision trace. 0 = the required process/package/control is absent, a required critical action/test is not implemented, or a critical blocking item remains open. | N/A - non-critical indicator | HRWHPI governance/evidence protocol; IFC Performance Standards effective 2012 PS1 as risk-management benchmark; WELL Health-Safety Rating Guidebook Q2 2021 as documentation/governance benchmark. | CR-01 v1.0 (2026-08-10); IFC PS (effective 2012) PS1 benchmark; WELL Health-Safety Guidebook Q2 2021 benchmark. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-GOV-04 | Mandatory | Stage-evidence matrix؛ required evidence completion by stage; maturity status of each indicator. | Stage checklist؛ evidence register؛ design/construction/commissioning/POE records. | Process / completeness / readiness | INDICATOR TEST — Stage-evidence matrix؛ required evidence completion by stage; maturity status of each indicator. 4 = 100% of the required package, actions, records, tests, and approvals for the indicator are complete, current, traceable, and Verified; critical open items = 0. | INDICATOR TEST — Stage-evidence matrix؛ required evidence completion by stage; maturity status of each indicator. 3 = >=90% to <100% complete/closed; critical open items = 0; only minor administrative gaps remain and traceability/readiness is not materially impaired. | INDICATOR TEST — Stage-evidence matrix؛ required evidence completion by stage; maturity status of each indicator. 2 = >=70% to <90% complete/closed OR one material non-critical open item remains; the process is still auditable and a corrective path is defined. | INDICATOR TEST — Stage-evidence matrix؛ required evidence completion by stage; maturity status of each indicator. 1 = >0% to <70% complete/closed OR multiple material open items/records are missing; closure/readiness is weak or poorly traceable. | INDICATOR TEST — Stage-evidence matrix؛ required evidence completion by stage; maturity status of each indicator. 0 = the required process/package/control is absent, a required critical action/test is not implemented, or a critical blocking item remains open. | N/A - non-critical indicator | HRWHPI governance/evidence protocol; IFC Performance Standards effective 2012 PS1 as risk-management benchmark; WELL Health-Safety Rating Guidebook Q2 2021 as documentation/governance benchmark. | CR-01 v1.0 (2026-08-10); IFC PS (effective 2012) PS1 benchmark; WELL Health-Safety Guidebook Q2 2021 benchmark. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.
V2-EVD-01 | Mandatory | Evidence completeness audit + traceability fields; separate status coding for NE versus NC. | Evidence matrix؛ document/test/measurement IDs؛ verifier/date؛ NE/NC status log. | Process / completeness / readiness | INDICATOR TEST — Evidence completeness audit + traceability fields; separate status coding for NE versus NC. 4 = 100% of the required package, actions, records, tests, and approvals for the indicator are complete, current, traceable, and Verified; critical open items = 0. | INDICATOR TEST — Evidence completeness audit + traceability fields; separate status coding for NE versus NC. 3 = >=90% to <100% complete/closed; critical open items = 0; only minor administrative gaps remain and traceability/readiness is not materially impaired. | INDICATOR TEST — Evidence completeness audit + traceability fields; separate status coding for NE versus NC. 2 = >=70% to <90% complete/closed OR one material non-critical open item remains; the process is still auditable and a corrective path is defined. | INDICATOR TEST — Evidence completeness audit + traceability fields; separate status coding for NE versus NC. 1 = >0% to <70% complete/closed OR multiple material open items/records are missing; closure/readiness is weak or poorly traceable. | INDICATOR TEST — Evidence completeness audit + traceability fields; separate status coding for NE versus NC. 0 = the required process/package/control is absent, a required critical action/test is not implemented, or a critical blocking item remains open. | N/A - non-critical indicator | HRWHPI evidence taxonomy/audit-trail protocol; IFC Performance Standards effective 2012 PS1; WELL Health-Safety Rating Guidebook Q2 2021 documentation/governance benchmark. | CR-01 v1.0 (2026-08-10); IFC PS (effective 2012) PS1 benchmark; WELL Health-Safety Guidebook Q2 2021 benchmark. CASE-LOCK RULE: the applicable mandatory clause/edition and any numeric benchmark denominator/target must be frozen in the evidence register before independent paired-rater scoring. | LOCKED | CR-01 v1.0 pre-IRR lock. Local/AHJ mandatory criteria prevail. Benchmark denominator/target/scenario set and source clause/version must be frozen before both raters score; changes require controlled re-release.

## WEIGHTS
HRWHPI Expert-Confirmed Locked Weights
Aggregate-only reproduction. No expert-level weighting records are included.
Domain_ID | Domain_Name | Locked_Domain_Weight | Points_of_100 | Indicator_Count | Lock_Status
D1 | Regulatory, Site & Access Governance | 11.01% |  |  | LOCKED
D2 | Spatial, Clinical & Women/Neonatal Planning | 11.52% |  |  | LOCKED
D3 | Vertical Transportation & Mobility Resilience | 9.946% |  |  | LOCKED
D4 | Fire & Life Safety | 12.18% |  |  | LOCKED
D5 | Critical MEP, Utilities & System Resilience | 16.27% |  |  | LOCKED
D6 | Environmental, Infection Control & Healing Environment | 8.754% |  |  | LOCKED
D7 | Constructability, Commissioning & Operational Readiness | 14.11% |  |  | LOCKED
D8 | Operations, Facilities & Lifecycle Performance | 9.688% |  |  | LOCKED
D9 | Digital Intelligence, Evidence & Governance | 6.52% |  |  | LOCKED
TOTAL
Indicator weights
Indicator_ID | Domain_ID | Class | Frozen_Wording | Global_Weight_Wj | Points_of_100
V2-REG-01 | D1 | Critical Gate | يوثق المشروع مسار الترخيص وموافقات الجهة ذات الاختصاص لكل مرحلة، مع حالة كل موافقة والاشتراطات المفتوحة والمانعة. | 1.492%
V2-REG-02 | D1 | Mandatory | يربط كل مؤشر قابل للامتثال بالمرجع الساري وإصدار الكود والبند أو منهج التحقق والجهة صاحبة الاختصاص. | 1.247%
V2-REG-03 | D1 | Mandatory | يوثق كل استثناء أو انحراف تنظيمي بمبرر فني وموافقة مكتوبة من الجهة المخولة قبل اعتباره مقبولًا. | 1.193%
V2-REG-04 | D1 | Mandatory | يميز HRWHPI بوضوح بين التقييم المبدئي قبل الترخيص والامتثال المثبت بعد استلام الوثائق والموافقات الرسمية. | 1.076%
V2-SIT-01 | D1 | Critical Gate | يثبت المشروع مشروعية الاستعمال والارتفاع والارتدادات ووصول الإطفاء والإسعاف قبل احتساب أي درجة أداء كلية. | 1.478%
V2-SIT-02 | D1 | Critical Gate | يفصل التصميم الخارجي بقدر الإمكان بين الإسعاف والإطفاء والخدمات والجمهور، ويختبر نقاط التقاطع المتبقية تحت الذروة والطوارئ. | 1.255%
V2-SIT-03 | D1 | Critical Gate | يحدد المشروع تعارضات الموقع وقدرة الكهرباء والمياه والصرف والخدمات الداعمة ويغلق المخاطر المانعة قبل اعتماد الموقع. | 1.397%
V2-SIT-04 | D1 | Performance | يقاس الوصول الصحي الآمن للمشاة في المناخ الحار بزمن ومسافة المشي والتظليل والراحة الحرارية والفصل عن المركبات وسهولة الحوامل وذوي الإعاقة. | 0.9823%
V2-SIT-05 | D1 | Performance | يقاس أداء المواقف والإنزال بزمن الوصول والبحث والانتظار وطول الطابور وأولوية الحوامل وذوي الإعاقة والفصل عن الإسعاف والخدمات. | 0.8876%
V2-SPA-01 | D2 | Performance | يثبت المشروع اتجاهًا أو مساحة توسع محمية واحتياطيات بنيوية وخدمية تسمح بالنمو دون الإخلال بالمخارج والنواة والمسارات الحرجة. | 1.076%
V2-SPA-02 | D2 | Performance | تثبت مرونة الطابق النموذجي بإمكانية تغيير الوظائف أو زيادة العناية دون أعمال إنشائية كبيرة أو تعطيل شامل. | 1.193%
V2-SPA-03 | D2 | Performance | يقيم تأثير النواة وشبكة الأعمدة وارتفاعات الطوابق ومساحة الروافع والفراغات الفنية على المرونة والكفاءة وقابلية إضافة أو تعديل الأنظمة. | 1.18%
V2-CLN-01 | D2 | Critical Gate | يقاس زمن الانتقال السريري للمسارات الحرجة مثل LDR–OR–NICU والطوارئ–التصوير/المختبر تحت سيناريوات تشغيل وذروة محددة. | 1.614%
V2-CLN-02 | D2 | Mandatory | تثبت العلاقات السريرية الحرجة بمصفوفة علاقات ومسافات ومحاكاة حركة وزمن بدل الاكتفاء بوصف «قريب/بعيد». | 1.614%
V2-CLN-03 | D2 | Critical Gate | يقلل التصميم تقاطع الحركة العامة والسريرية والخدمية ويثبت الفصل والتحكم في نقاط العبور والمصاعد المشتركة. | 1.614%
V2-CLN-04 | D2 | Mandatory | تقاس الخصوصية وتجربة الأسرة في خدمات النساء والولادة وNICU بخطوط الرؤية وفصل المسارات والتحكم بالدخول وملاءمة وجود الأسرة. | 1.614%
V2-NIC-01 | D2 | Critical Gate | تثبت بيئات NICU وحديثي الولادة استقرار الظروف البيئية والهدوء والمرونة والتنسيق الخدمي داخل المساحات الحساسة. | 1.614%
V2-VRT-01 | D3 | Mandatory | يحدد عدد وتخصيص المصاعد من نموذج طلب فعلي للأسرة والمرضى والمواد والزوار وفترات الذروة، لا من العدد الإجمالي فقط. | 2.394%
V2-VRT-02 | D3 | Performance | يقاس أداء النقل الرأسي بأزمنة الانتظار والرحلة والمناولة ومستوى الخدمة لكل فئة حركة حرجة وعادية. | 2.102%
V2-VRT-03 | D3 | Critical Gate | تتوفر مرونة N-1 أو بديل تشغيلي مكافئ للنقل الرأسي الحرج وفق تحليل الخطورة، بما يشمل الصيانة المخططة لا الطوارئ فقط. | 2.725%
V2-VRT-04 | D3 | Critical Gate | تثبت استمرارية المصاعد ومسارات النقل الحرج أثناء الطوارئ والاختبارات والربط المرحلي مع وجود سعة بديلة وخطة rollback. | 2.725%
V2-FIR-01 | D4 | Critical Gate | يثبت التصميم استراتيجية دفاع في المكان وتقسيمًا أفقيًا وإخلاءً مرحليًا مناسبًا لمرضى محدودي الحركة والمواليد. | 2.185%
V2-FIR-02 | D4 | Critical Gate | تثبت مخارج الهروب وسعاتها واستمراريتها وعدم إعاقتها للمرضى والعاملين تحت سيناريوات الإشغال والطوارئ. | 1.982%
V2-FIR-03 | D4 | Critical Gate | تتحقق أنظمة التحكم في الدخان بالقياس تحت الحالات العادية وأوضاع الفشل والطاقة الاحتياطية وفق أساس تصميم واضح. | 1.93%
V2-FIR-04 | D4 | Critical Gate | تدار سلامة الحواجز والأبواب والاختراقات طوال التنفيذ والتشغيل بسجل قابل للتتبع وفحص قبل الإغلاق وبعد كل تعديل. | 1.878%
V2-FIR-05 | D4 | Critical Gate | تختبر وظائف الإنذار والرش والأبواب والدخان والمصاعد والطاقة والمضخات كمنظومة مترابطة مع التحقق من التوقيت والعودة للوضع الطبيعي. | 2.148%
V2-FIR-06 | D4 | Critical Gate | يقاس زمن الإخلاء المرحلي للانتقال إلى حجرة آمنة ثم للمراحل اللاحقة عند الحاجة وفق خصائص مرضى مستشفى النساء والمواليد. | 2.06%
V2-MEP-01 | D5 | Critical Gate | تثبت منظومة الطاقة الحرجة التكرار والتحويل الآمن واستمرار الأحمال السريرية الحرجة أثناء فقد المصدر والصيانة. | 2.234%
V2-MEP-02 | D5 | Critical Gate | تحافظ أنظمة HVAC للمناطق الحرجة على الضغط والحرارة والرطوبة والترشيح أثناء التشغيل الطبيعي وأوضاع الفشل المحددة. | 2.234%
V2-MEP-03 | D5 | Critical Gate | تثبت شبكة الغازات الطبية نقاء وضغط وإنذارات وتكرارًا مناسبًا للمناطق الحرجة وتستمر أثناء الفشل والصيانة المخططة. | 2.182%
V2-MEP-04 | D5 | Critical Gate | تثبت أنظمة المياه والصرف الاستقلال/الاحتياط وجودة المياه ومنع الارتداد والاستجابة للتسربات دون تعطيل سريري غير مقبول. | 2.075%
V2-RES-01 | D5 | Performance | تقاس اعتمادية الأنظمة الحرجة بالتوافر Availability وزمن الاستعادة وMTTR من بيانات تشغيل فعلية أو اختبارات فشل موحدة. | 1.688%
V2-RES-02 | D5 | Critical Gate | تثبت الأنظمة الحرجة قابلية العزل والتكرار واستمرار الخدمة أثناء الفشل والصيانة المخططة وفق تحليل الخطورة. | 2.106%
V2-RES-03 | D5 | Mandatory | تختبر سيناريوهات Multi-hazard المركبة التي تجمع أخطارًا مترابطة ذات صلة بالموقع والتشغيل بدل اختبار كل نظام منفردًا فقط. | 1.595%
V2-RES-04 | D5 | Critical Gate | ينفذ اختبار سيناريو انقطاع موثق لكل نظام حرج لإثبات الاستمرارية والتحويل والعودة الآمنة، لا مجرد مراجعة وجود معدات احتياطية. | 2.16%
V2-ENV-01 | D6 | Critical Gate | يطبق ICRA قبل وأثناء الأعمال المرتبطة بمنشأة عاملة مع حواجز وضغط ومسارات عمال ونفايات ورصد وتنظيف متوافق مع مستوى الخطورة. | 1.794%
V2-ENV-02 | D6 | Mandatory | يفصل تدفق النفايات والبياضات والتنظيف عن الجمهور والمسارات النظيفة مع سعة تخزين مؤقت وظروف بيئية مناسبة. | 1.424%
V2-ENV-03 | D6 | Critical Gate | يقيّم خطر جودة الهواء عند مآخذ الهواء بالنسبة للغبار والعوادم والمولدات والتحميل واتجاهات الرياح ويعالج مصادر التلوث غير المقبولة. | 1.693%
V2-ENV-04 | D6 | Performance | يقيس المشروع تعرض المستخدمين والمداخل والفراغات الخارجية للحرارة والغبار والضوضاء والتلوث ويطبق تخفيفًا قابلًا للتحقق. | 1.264%
V2-ENV-05 | D6 | Performance | تقاس النظافة التشغيلية في المناطق الحرجة ومسارات الدعم بمؤشرات تدقيق وبلاغات واستجابة قابلة للتتبع، لا بوصف عام فقط. | 1.53%
V2-ENV-06 | D6 | Enhancement | تختبر جودة الضوء الطبيعي والوهج والراحة الحرارية وخطوط الرؤية والخصوصية في الفراغات السريرية بدل الاعتماد على مساحة الزجاج وحدها. | 1.05%
V2-CON-01 | D7 | Mandatory | تقاس جاهزية التصميم للتنفيذ بمستوى التنسيق والتعارضات المفتوحة وRFIs وجاهزية shop drawings ومساحات التركيب والصيانة. | 1.327%
V2-CON-02 | D7 | Mandatory | يقاس نضج BIM والتنسيق متعدد التخصصات بكثافة التعارضات الحرجة المفتوحة واكتمال النموذج ومسؤوليات التحقق قبل الطرح والتنفيذ. | 1.141%
V2-CON-03 | D7 | Critical Gate | تحدد نقاط توقف Hold Points للأعمال المخفية الحرجة قبل إغلاق الأسقف والجدران مع أدلة قبول إلزامية. | 1.516%
V2-CON-04 | D7 | Performance | تقاس جودة التنفيذ بنسبة نجاح الفحص والاختبار من أول مرة واتجاه NCR وإعادة العمل في الحزم الحرجة. | 1.215%
V2-CON-05 | D7 | Critical Gate | تثبت خطط التنفيذ داخل مستشفى عامل فصل الإنشاء عن المرضى والإسعاف والخدمات واستمرارية التشغيل أثناء الرفع والربط والاختبار. | 1.739%
V2-CON-06 | D7 | Mandatory | يكتمل ملف الفحص والاختبار لكل حزمة حرجة قبل القبول، مع ربط النتائج بالعيوب والتصحيح وإعادة الاختبار. | 1.357%
V2-COM-01 | D7 | Mandatory | تكتمل أعمال Commissioning للأنظمة الحرجة بقبول قائم على الأداء والاختبار والاتجاهات لا على الشهادات المنفردة فقط. | 1.473%
V2-COM-02 | D7 | Critical Gate | تنفذ اختبارات تكامل للواجهات بين الطاقة والحريق والدخان والمصاعد وBMS والأنظمة الحرجة ذات الصلة وفق سيناريوات فشل وعودة للوضع الطبيعي. | 1.672%
V2-OPS-01 | D7 | Mandatory | تقاس الجاهزية التشغيلية قبل التسليم باكتمال الأعمال والاختبارات والوثائق والتدريب وقطع الغيار والتصاريح وخطة الانتقال. | 1.468%
V2-OPS-02 | D7 | Mandatory | يكتمل ملف تسليم الأصول الرقمي والتشغيلي بما يسمح بالتشغيل والصيانة والتتبع بعد الاستلام. | 1.202%
V2-OPS-03 | D8 | Performance | تقاس كثافة الاستخدام والذروة الفعلية للفراغات والمصاعد والخدمات لتحديد الفجوة بين افتراضات التصميم والتشغيل. | 0.7364%
V2-LIF-01 | D8 | Mandatory | تثبت قابلية صيانة الأنظمة والمعدات من حيث الوصول والعزل ومساحة العمل وزمن الإصلاح دون تعطيل سريري غير مقبول. | 1.06%
V2-LIF-02 | D8 | Mandatory | يثبت لكل معدة كبيرة أو حرجة مسار إدخال واستبدال قابل للتنفيذ بعد التشغيل مع الأبعاد والأحمال ونقاط الرفع ومناطق العزل. | 0.8914%
V2-LIF-03 | D8 | Mandatory | تقاس جاهزية قطع الغيار الحرجة بالتوفر ومعدل التغطية وزمن التوريد بما يتوافق مع مخاطر وتعطل كل أصل حرج. | 0.952%
V2-LIF-04 | D8 | Mandatory | تثبت تغطية المهارات الفنية الحرجة في كل وردية مع زمن استجابة وإجراءات طوارئ وأدوات مناسبة للأصول الحرجة. | 1.059%
V2-LIF-05 | D8 | Performance | يقاس زمن الاستجابة والإصلاح للأعطال الحرجة والمتكررة ويستخدم الاتجاه لتحديد ضعف قابلية الصيانة أو الموارد. | 0.9778%
V2-LIF-06 | D8 | Performance | تثبت قابلية تجديد أو استبدال المكونات أثناء استمرار التشغيل من خلال العزل المرحلي والمسارات والبدائل المؤقتة. | 0.9247%
V2-LIF-07 | D8 | Performance | تراقب حالة التشطيبات والحواجز ذات الأثر على العدوى والحريق والتشغيل وتغلق العيوب بحسب خطورتها. | 0.7045%
V2-LIF-08 | D8 | Mandatory | ينفذ تقييم ما بعد الإشغال للتحقق من الأداء الفعلي للحركة والبيئة والصيانة وتجربة المستخدم مقارنة بافتراضات التصميم. | 0.9487%
V2-LIF-09 | D8 | Performance | تسجل فجوات التصميم–التشغيل المكتشفة بعد الإشغال وتغلق بإجراءات تصحيح مع مسؤولية وموعد وإثبات أثر. | 0.8114%
V2-LIF-10 | D8 | Performance | تقارن البدائل على تكلفة دورة الحياة بما يشمل CAPEX وOPEX والصيانة والاستبدال ضمن افتراضات موثقة ومخاطر تشغيلية. | 0.6219%
V2-DIG-01 | D9 | Mandatory | تقاس جودة بيانات BMS/CMMS من الاكتمال والصحة والتوقيت وقابلية ربط الأصل والإنذار وأمر العمل بما يسمح باستخدامها في القرار والتحقق. | 0.6479%
V2-DIG-02 | D9 | Performance | تقاس جودة إدارة الإنذارات بمعدل الإنذارات الكاذبة والمتكررة وأولوية الإنذار وزمن الاستجابة بعد rationalization. | 0.5854%
V2-DIG-03 | D9 | Enhancement | تستخدم مؤشرات اتجاه وتدهور قابلة للتحقق للكشف المبكر عن فشل الأنظمة الحرجة وربطها بصيانة تنبؤية. | 0.4991%
V2-DIG-04 | D9 | Mandatory | يحدد مستوى نضج BIM واكتمال بيانات النموذج اللازمة للتحقق من المساحات والعلاقات والتعارضات والتسليم التشغيلي. | 0.6029%
V2-DIG-05 | D9 | Mandatory | ترتبط القرارات الحسابية أو المحاكاة بمسؤول تصميم محدد ومدخلات ونسخة نموذج ونتائج قابلة لإعادة التحقق، ولا تقبل الأوصاف النصية وحدها. | 0.684%
V2-GOV-01 | D9 | Critical Gate | تطبق بوابات Go/No-Go مرحلية تمنع الانتقال عند فشل متطلب حرج غير قابل للتعويض ولا يسمح المتوسط الكلي بتجاوز الفشل. | 0.8398%
V2-GOV-02 | D9 | Mandatory | يخضع كل تغيير بعد تجميد التصميم لتقييم أثر موثق على السلامة والتشغيل والتكلفة والبرنامج والموافقات قبل التنفيذ. | 0.7674%
V2-GOV-03 | D9 | Mandatory | توثق مقارنة البدائل التصميمية بمعايير وأوزان وافتراضات ومخاطر ونتائج قابلة للتدقيق قبل تثبيت البديل. | 0.5645%
V2-GOV-04 | D9 | Mandatory | تختلف متطلبات دليل HRWHPI ودرجة نضج الإثبات حسب مرحلة الجدوى والتصميم والتنفيذ والتشغيل وما بعد الإشغال مع عدم مساواة الدليل المبدئي بالدليل النهائي. | 0.634%
V2-EVD-01 | D9 | Mandatory | يرتبط كل مؤشر بحزمة دليل قابلة للتدقيق تحدد نوع الدليل ومصدره وتاريخه ومرحلة التقييم ومسؤول التحقق وحالة Not Evidenced منفصلة عن Non-Compliant. | 0.6947%
TOTAL
Note on A1: Source SHA-256: fd8639d8be8f00c0caab949d3b6bc00cc7ec40fa12f1e63a346d915abc8a58e7

## CONTENT_VALIDATION
Aggregate Delphi Round 1 Content Validation — 72 Indicators
Aggregate positive-category counts only. Positive = rating 3 or 4. Exact 3-versus-4 responses are not reconstructed; no expert identifiers are included.
Indicator_ID | Domain | Class | Eligible_N | Rel_Positive | I-CVI_Rel | Pc_Rel | Kappa_Rel | Clar_Positive | I-CVI_Clar | Pc_Clar | Kappa_Clar | Meas_Positive | I-CVI_Meas | Pc_Meas | Kappa_Meas | Gate_Yes | Gate_No | Gate_Unsure | Gate_Class_Agr | Keep | Modify | Merge | Delete | Change_Prop | R2_Required
V2-REG-01 | Regulatory legitimacy | Critical Gate | 3 | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 3 | 0 | 0 |  | 3 | 0 | 0 | 0
V2-REG-02 | Regulatory legitimacy | Mandatory | 3 | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 0 | 3 | 0 |  | 3 | 0 | 0 | 0
V2-REG-03 | Regulatory legitimacy | Mandatory | 3 | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 0 | 3 | 0 |  | 3 | 0 | 0 | 0
V2-REG-04 | Regulatory legitimacy | Mandatory | 3 | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 0 | 3 | 0 |  | 3 | 0 | 0 | 0
V2-SIT-01 | Site & regulatory safety | Critical Gate | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 | 0 | 0 |  | 4 | 0 | 0 | 0
V2-SIT-02 | Site & access performance | Critical Gate | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 | 0 | 0 |  | 4 | 0 | 0 | 0
V2-SIT-03 | Site & infrastructure | Critical Gate | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 5 | 0 | 0 |  | 5 | 0 | 0 | 0
V2-SIT-04 | Site & climate performance | Performance | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 0 | 4 | 0 |  | 4 | 0 | 0 | 0
V2-SIT-05 | Site & access performance | Performance | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 0 | 4 | 0 |  | 4 | 0 | 0 | 0
V2-SPA-01 | Spatial & future adaptability | Performance | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 0 | 4 | 0 |  | 4 | 0 | 0 | 0
V2-SPA-02 | Spatial & future adaptability | Performance | 3 | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 0 | 3 | 0 |  | 3 | 0 | 0 | 0
V2-SPA-03 | Spatial & technical adaptability | Performance | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-CLN-01 | Clinical time-criticality | Critical Gate | 3 | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 3 | 0 | 0 |  | 3 | 0 | 0 | 0
V2-CLN-02 | Clinical time-criticality | Mandatory | 3 | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 0 | 3 | 0 |  | 3 | 0 | 0 | 0
V2-CLN-03 | Clinical circulation | Critical Gate | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 | 0 | 0 |  | 4 | 0 | 0 | 0
V2-CLN-04 | Patient & family-centered care | Mandatory | 3 | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 0 | 3 | 0 |  | 3 | 0 | 0 | 0
V2-NIC-01 | Women & neonatal clinical environment | Critical Gate | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 | 0 | 0 |  | 4 | 0 | 0 | 0
V2-VRT-01 | Vertical resilience | Mandatory | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 0 | 4 | 0 |  | 4 | 0 | 0 | 0
V2-VRT-02 | Vertical resilience | Performance | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-VRT-03 | Vertical resilience | Critical Gate | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 | 0 | 0 |  | 4 | 0 | 0 | 0
V2-VRT-04 | Vertical resilience | Critical Gate | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 | 0 | 0 |  | 4 | 0 | 0 | 0
V2-FIR-01 | Fire & life safety | Critical Gate | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 5 | 0 | 0 |  | 5 | 0 | 0 | 0
V2-FIR-02 | Fire & life safety | Critical Gate | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 5 | 0 | 0 |  | 5 | 0 | 0 | 0
V2-FIR-03 | Fire & life safety | Critical Gate | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 5 | 0 | 0 |  | 5 | 0 | 0 | 0
V2-FIR-04 | Fire & life safety | Critical Gate | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 | 0 | 0 |  | 4 | 0 | 0 | 0
V2-FIR-05 | Fire & life safety | Critical Gate | 7 | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  | 7 | 0 | 0 |  | 7 | 0 | 0 | 0
V2-FIR-06 | Fire & life safety | Critical Gate | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 | 0 | 0 |  | 4 | 0 | 0 | 0
V2-MEP-01 | Critical utilities | Critical Gate | 6 | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 6 | 0 | 0 |  | 6 | 0 | 0 | 0
V2-MEP-02 | Critical utilities | Critical Gate | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 5 | 0 | 0 |  | 5 | 0 | 0 | 0
V2-MEP-03 | Critical utilities | Critical Gate | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 5 | 0 | 0 |  | 5 | 0 | 0 | 0
V2-MEP-04 | Critical utilities | Critical Gate | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 5 | 0 | 0 |  | 5 | 0 | 0 | 0
V2-RES-01 | Resilience & reliability | Performance | 6 | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 0 | 6 | 0 |  | 6 | 0 | 0 | 0
V2-RES-02 | Resilience & reliability | Critical Gate | 6 | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 6 | 0 | 0 |  | 6 | 0 | 0 | 0
V2-RES-03 | Resilience & emergency readiness | Mandatory | 6 | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 0 | 6 | 0 |  | 6 | 0 | 0 | 0
V2-RES-04 | Resilience & emergency readiness | Critical Gate | 7 | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  | 7 | 0 | 0 |  | 7 | 0 | 0 | 0
V2-ENV-01 | Environmental & infection safety | Critical Gate | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 5 | 0 | 0 |  | 5 | 0 | 0 | 0
V2-ENV-02 | Environmental & infection safety | Mandatory | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 0 | 4 | 0 |  | 4 | 0 | 0 | 0
V2-ENV-03 | Environmental & infection safety | Critical Gate | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 | 0 | 0 |  | 4 | 0 | 0 | 0
V2-ENV-04 | Environmental & climate performance | Performance | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-ENV-05 | Environmental & operational hygiene | Performance | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 0 | 4 | 0 |  | 4 | 0 | 0 | 0
V2-ENV-06 | Healing environment & climate | Enhancement | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-CON-01 | Constructability & delivery | Mandatory | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-CON-02 | Constructability & digital coordination | Mandatory | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 0 | 4 | 0 |  | 4 | 0 | 0 | 0
V2-CON-03 | Construction quality | Critical Gate | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 | 0 | 0 |  | 4 | 0 | 0 | 0
V2-CON-04 | Construction quality | Performance | 3 | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 0 | 3 | 0 |  | 3 | 0 | 0 | 0
V2-CON-05 | Construction continuity | Critical Gate | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 5 | 0 | 0 |  | 5 | 0 | 0 | 0
V2-CON-06 | Construction quality | Mandatory | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 0 | 4 | 0 |  | 4 | 0 | 0 | 0
V2-COM-01 | Commissioning & handover | Mandatory | 7 | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  | 0 | 7 | 0 |  | 7 | 0 | 0 | 0
V2-COM-02 | Commissioning & handover | Critical Gate | 7 | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  | 7 | 0 | 0 |  | 7 | 0 | 0 | 0
V2-OPS-01 | Operational readiness | Mandatory | 7 | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  | 0 | 7 | 0 |  | 7 | 0 | 0 | 0
V2-OPS-02 | Asset handover | Mandatory | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-OPS-03 | Operational performance | Performance | 6 | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 0 | 6 | 0 |  | 6 | 0 | 0 | 0
V2-LIF-01 | Lifecycle performance | Mandatory | 7 | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  | 0 | 7 | 0 |  | 7 | 0 | 0 | 0
V2-LIF-02 | Lifecycle performance | Mandatory | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-LIF-03 | Lifecycle performance | Mandatory | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-LIF-04 | Lifecycle performance | Mandatory | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-LIF-05 | Lifecycle performance | Performance | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-LIF-06 | Lifecycle performance | Performance | 6 | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 0 | 6 | 0 |  | 6 | 0 | 0 | 0
V2-LIF-07 | Lifecycle performance | Performance | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 0 | 4 | 0 |  | 4 | 0 | 0 | 0
V2-LIF-08 | Lifecycle performance | Mandatory | 6 | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 0 | 6 | 0 |  | 6 | 0 | 0 | 0
V2-LIF-09 | Lifecycle performance | Performance | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-LIF-10 | Lifecycle performance | Performance | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-DIG-01 | Digital asset intelligence | Mandatory | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 0 | 4 | 0 |  | 4 | 0 | 0 | 0
V2-DIG-02 | Digital asset intelligence | Performance | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 0 | 4 | 0 |  | 4 | 0 | 0 | 0
V2-DIG-03 | Digital asset intelligence | Enhancement | 3 | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 0 | 3 | 0 |  | 3 | 0 | 0 | 0
V2-DIG-04 | Digital coordination | Mandatory | 4 | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 0 | 4 | 0 |  | 4 | 0 | 0 | 0
V2-DIG-05 | Evidence-based design | Mandatory | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-GOV-01 | Governance & safety gates | Critical Gate | 6 | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 6 | 0 | 0 |  | 6 | 0 | 0 | 0
V2-GOV-02 | Governance & change control | Mandatory | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-GOV-03 | Governance & decision quality | Mandatory | 5 | 5 |  |  |  | 5 |  |  |  | 5 |  |  |  | 0 | 5 | 0 |  | 5 | 0 | 0 | 0
V2-GOV-04 | Lifecycle governance | Mandatory | 6 | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 0 | 6 | 0 |  | 6 | 0 | 0 | 0
V2-EVD-01 | Evidence traceability | Mandatory | 9 | 9 |  |  |  | 9 |  |  |  | 9 |  |  |  | 0 | 9 | 0 |  | 9 | 0 | 0 | 0
Note on A1: Source SHA-256: ca772f609e5b20c525c631871ebef1f31d56b4d6f21040c0eaecaa71add5ecc0

## CV_SUMMARY
Content-Validation Summary
Derived directly from the aggregate item-level counts in CONTENT_VALIDATION.
Metric | Observed | Interpretation | Status | Notes
Indicator count |  | Frozen denominator |  | 72 expected
S-CVI/Ave — Relevance |  | Average item relevance CVI
S-CVI/Ave — Clarity |  | Average item clarity CVI
S-CVI/Ave — Measurability |  | Average item measurability CVI
S-CVI/Ave — overall |  | Overall average across the three content-validity dimensions
S-CVI/UA |  | Universal agreement across all three CVI dimensions
Mean modified kappa |  | Chance-corrected content validity
Gate/class agreement |  | Agreement with proposed gate/non-gate classification
Unanimous Keep proportion |  | Indicators unanimously kept
Indicators requiring Round 2 |  | Unresolved items under the pre-specified R2 rule |  | Round 2 is not artificially created when no unresolved item remains.

## IRR_PAIRED
Anonymized Paired Ratings — Stage 7 Controlled Calibration IRR
Rater identities are removed. These paired ratings support the reliability calculations only and are not Mayo final case scores.
Indicator_ID | Domain_ID | Class | Rater_1_Score | Rater_2_Score | Abs_Diff | Exact_Agree | Within_1 | Rater_1_Gate | Rater_2_Gate | Gate_Pair_Valid | Gate_Exact | Gate_Discordance | Decision_Changing_Unresolved
V2-REG-01 | D1 | Critical Gate | 4 | 4 |  |  |  | PASS | PASS
V2-REG-02 | D1 | Mandatory | 3 | 3
V2-REG-03 | D1 | Mandatory | 3 | 3
V2-REG-04 | D1 | Mandatory | 2 | 2
V2-SIT-01 | D1 | Critical Gate | 3 | 3 |  |  |  | PASS | PASS
V2-SIT-02 | D1 | Critical Gate | 4 | 4 |  |  |  | PASS | PASS
V2-SIT-03 | D1 | Critical Gate | 3 | 3 |  |  |  | PASS | PASS
V2-SIT-04 | D1 | Performance | 2 | 3
V2-SIT-05 | D1 | Performance | 4 | 4
V2-SPA-01 | D2 | Performance | 2 | 3
V2-SPA-02 | D2 | Performance | 3 | 3
V2-SPA-03 | D2 | Performance | 2 | 2
V2-CLN-01 | D2 | Critical Gate | 3 | 3 |  |  |  | PASS | PASS
V2-CLN-02 | D2 | Mandatory | 2 | 3
V2-CLN-03 | D2 | Critical Gate | 3 | 3 |  |  |  | PASS | PASS
V2-CLN-04 | D2 | Mandatory | 2 | 3
V2-NIC-01 | D2 | Critical Gate | 3 | 3 |  |  |  | PASS | PASS
V2-VRT-01 | D3 | Mandatory | 3 | 2
V2-VRT-02 | D3 | Performance | 3 | 3
V2-VRT-03 | D3 | Critical Gate | 3 | 2 |  |  |  | PASS | PASS
V2-VRT-04 | D3 | Critical Gate | 4 | 4 |  |  |  | PASS | PASS
V2-FIR-01 | D4 | Critical Gate | 3 | 3 |  |  |  | PASS | PASS
V2-FIR-02 | D4 | Critical Gate | 3 | 3 |  |  |  | PASS | PASS
V2-FIR-03 | D4 | Critical Gate | 4 | 4 |  |  |  | PASS | PASS
V2-FIR-04 | D4 | Critical Gate | 3 | 2 |  |  |  | PASS | PASS
V2-FIR-05 | D4 | Critical Gate | 4 | 4 |  |  |  | PASS | PASS
V2-FIR-06 | D4 | Critical Gate | 3 | 3 |  |  |  | PASS | PASS
V2-MEP-01 | D5 | Critical Gate | 3 | 2 |  |  |  | PASS | PASS
V2-MEP-02 | D5 | Critical Gate | 4 | 4 |  |  |  | PASS | PASS
V2-MEP-03 | D5 | Critical Gate | 3 | 3 |  |  |  | PASS | PASS
V2-MEP-04 | D5 | Critical Gate | 4 | 4 |  |  |  | PASS | PASS
V2-RES-01 | D5 | Performance | 3 | 2
V2-RES-02 | D5 | Critical Gate | 3 | 3 |  |  |  | PASS | PASS
V2-RES-03 | D5 | Mandatory | 3 | 3
V2-RES-04 | D5 | Critical Gate | 3 | 3 |  |  |  | PASS | PASS
V2-ENV-01 | D6 | Critical Gate | 4 | 4 |  |  |  | PASS | PASS
V2-ENV-02 | D6 | Mandatory | 4 | 4
V2-ENV-03 | D6 | Critical Gate | 3 | 2 |  |  |  | PASS | PASS
V2-ENV-04 | D6 | Performance | 2 | 2
V2-ENV-05 | D6 | Performance | 3 | 3
V2-ENV-06 | D6 | Enhancement | 2 | 3
V2-CON-01 | D7 | Mandatory | 3 | 3
V2-CON-02 | D7 | Mandatory | 3 | 3
V2-CON-03 | D7 | Critical Gate | 4 | 4 |  |  |  | PASS | PASS
V2-CON-04 | D7 | Performance | 4 | 4
V2-CON-05 | D7 | Critical Gate | 4 | 4 |  |  |  | PASS | PASS
V2-CON-06 | D7 | Mandatory | 2 | 2
V2-COM-01 | D7 | Mandatory | 3 | 3
V2-COM-02 | D7 | Critical Gate | 4 | 4 |  |  |  | PASS | PASS
V2-OPS-01 | D7 | Mandatory | 3 | 3
V2-OPS-02 | D7 | Mandatory | 3 | 3
V2-OPS-03 | D8 | Performance | 2 | 2
V2-LIF-01 | D8 | Mandatory | 4 | 4
V2-LIF-02 | D8 | Mandatory | 3 | 3
V2-LIF-03 | D8 | Mandatory | 2 | 2
V2-LIF-04 | D8 | Mandatory | 3 | 3
V2-LIF-05 | D8 | Performance | 4 | 4
V2-LIF-06 | D8 | Performance | 3 | 3
V2-LIF-07 | D8 | Performance | 3 | 3
V2-LIF-08 | D8 | Mandatory | 2 | 2
V2-LIF-09 | D8 | Performance | 4 | 4
V2-LIF-10 | D8 | Performance | 3 | 3
V2-DIG-01 | D9 | Mandatory | 2 | 2
V2-DIG-02 | D9 | Performance | 3 | 3
V2-DIG-03 | D9 | Enhancement | 3 | 3
V2-DIG-04 | D9 | Mandatory | 2 | 3
V2-DIG-05 | D9 | Mandatory | 3 | 3
V2-GOV-01 | D9 | Critical Gate | 3 | 3 |  |  |  | PASS | PASS
V2-GOV-02 | D9 | Mandatory | 4 | 4
V2-GOV-03 | D9 | Mandatory | 3 | 3
V2-GOV-04 | D9 | Mandatory | 2 | 2
V2-EVD-01 | D9 | Mandatory | 3 | 3

## IRR_CALC (hidden)
IRR Calculation Matrices
Quadratic weighted Cohen kappa for ordinal 0–4 scores and conventional Cohen kappa for Critical Gate categories.
Observed 5×5 score matrix | [6 empty] | Critical Gate 3×3 matrix
R1\R2 | 0 | 1 | 2 | 3 | 4 | Row total | R1\R2 | PASS | FAIL | NOT EVIDENCED | Row total
0 | [6 empty] | PASS
1 | [6 empty] | FAIL
2 | [6 empty] | NOT EVIDENCED
3 | [6 empty] | Col total
4
Col total
Observed agreement (Po)
Expected agreement (Pe)
Quadratic disagreement weights | 0 | 1 | 2 | 3 | 4 |  | Cohen kappa
0
1
2
3
4
Expected counts under independence
| 0 | 1 | 2 | 3 | 4
0
1
2
3
4
Observed weighted disagreement
Expected weighted disagreement
Quadratic weighted Cohen kappa

## IRR_SUMMARY
Final Inter-Rater Reliability Summary
Acceptance criteria were pre-specified before ratings. All score comparisons shown here are derived from the anonymized paired data.
Metric | Observed | Acceptance criterion | Status | Interpretation
Ordinal paired score count |  | 72 |  | 72 paired scores expected.
Quadratic weighted Cohen kappa |  | 0.8 |  | Primary ordinal IRR metric.
Exact score agreement |  | 70% |  | 60/72 expected in the frozen dataset.
Within-1 score agreement |  | 95% |  | All differences should be ≤1 for PASS.
Mean absolute difference |  | 0.5 |  | Lower is better.
Critical Gate paired count |  | 27 |  | All Critical Gates paired.
Critical Gate Cohen kappa |  | 0.8 |  | When Pe=1, kappa is mathematically not estimable.
Critical Gate exact agreement |  | 90% |  | Exact categorical agreement.
Decision-changing unresolved gate discordance |  | 0 |  | Must be zero.
Overall Stage 7 interpretation |  | All estimable pre-specified criteria pass |  | Gate kappa may be not estimable while exact gate agreement remains reportable.
Note on A1: Source SHA-256: 9820a64e65d8725c4a3aa0954b4398c6c36b5ed131bf0352bd7d26ad9a935a68

## MAYO_EVIDENCE
Mayo/Riyadh Evidence-Constrained Real-Case — Aggregate Evidence Status | [9 empty] | Evidence-coverage summary
No restricted project technical records, detailed plans, Fire Strategy, MEP files, lift studies, commissioning records, or simulated case-performance scores are included. | [9 empty] | Metric | Observed
Total indicators
Indicator_ID | Domain_ID | Class | Global_Weight_Wj | Manual_Evidence_Status | Evidence_Sufficiency | Case_Benchmark_Lock | Authentic_Context | Final_Score_Eligible | Critical_Gate_Outcome | Indicators with authentic context
V2-REG-01 | D1 | Critical Gate | 1.492% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED | Context count coverage
V2-REG-02 | D1 | Mandatory | 1.247% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A | Weighted authentic context coverage
V2-REG-03 | D1 | Mandatory | 1.193% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A | Final-score-eligible indicators
V2-REG-04 | D1 | Mandatory | 1.076% | Preliminary | Contextual only - insufficient to score | NOT LOCKED |  |  | N/A | Critical Gates total
V2-SIT-01 | D1 | Critical Gate | 1.478% | Preliminary | Contextual only - insufficient to score | NOT LOCKED |  |  | NOT EVIDENCED | Critical Gates with authentic context
V2-SIT-02 | D1 | Critical Gate | 1.255% | Preliminary | Contextual only - insufficient to score | NOT LOCKED |  |  | NOT EVIDENCED | Critical Gates resolved
V2-SIT-03 | D1 | Critical Gate | 1.397% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED | Complete-project HRWHPI | WITHHELD / NOT COMPUTABLE
V2-SIT-04 | D1 | Performance | 0.9823% | Preliminary | Contextual only - insufficient to score | NOT LOCKED |  |  | N/A
V2-SIT-05 | D1 | Performance | 0.8876% | Preliminary | Contextual only - insufficient to score | NOT LOCKED |  |  | N/A
V2-SPA-01 | D2 | Performance | 1.076% | Preliminary | Contextual only - insufficient to score | NOT LOCKED |  |  | N/A
V2-SPA-02 | D2 | Performance | 1.193% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-SPA-03 | D2 | Performance | 1.18% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-CLN-01 | D2 | Critical Gate | 1.614% | Preliminary | Contextual only - insufficient to score | NOT LOCKED |  |  | NOT EVIDENCED
V2-CLN-02 | D2 | Mandatory | 1.614% | Preliminary | Contextual only - insufficient to score | NOT LOCKED |  |  | N/A
V2-CLN-03 | D2 | Critical Gate | 1.614% | Preliminary | Contextual only - insufficient to score | NOT LOCKED |  |  | NOT EVIDENCED
V2-CLN-04 | D2 | Mandatory | 1.614% | Preliminary | Contextual only - insufficient to score | NOT LOCKED |  |  | N/A
V2-NIC-01 | D2 | Critical Gate | 1.614% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-VRT-01 | D3 | Mandatory | 2.394% | Preliminary | Contextual only - insufficient to score | NOT LOCKED |  |  | N/A
V2-VRT-02 | D3 | Performance | 2.102% | Preliminary | Contextual only - insufficient to score | NOT LOCKED |  |  | N/A
V2-VRT-03 | D3 | Critical Gate | 2.725% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-VRT-04 | D3 | Critical Gate | 2.725% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-FIR-01 | D4 | Critical Gate | 2.185% | Preliminary | Contextual only - insufficient to score | NOT LOCKED |  |  | NOT EVIDENCED
V2-FIR-02 | D4 | Critical Gate | 1.982% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-FIR-03 | D4 | Critical Gate | 1.93% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-FIR-04 | D4 | Critical Gate | 1.878% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-FIR-05 | D4 | Critical Gate | 2.148% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-FIR-06 | D4 | Critical Gate | 2.06% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-MEP-01 | D5 | Critical Gate | 2.234% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-MEP-02 | D5 | Critical Gate | 2.234% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-MEP-03 | D5 | Critical Gate | 2.182% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-MEP-04 | D5 | Critical Gate | 2.075% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-RES-01 | D5 | Performance | 1.688% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-RES-02 | D5 | Critical Gate | 2.106% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-RES-03 | D5 | Mandatory | 1.595% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-RES-04 | D5 | Critical Gate | 2.16% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-ENV-01 | D6 | Critical Gate | 1.794% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-ENV-02 | D6 | Mandatory | 1.424% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-ENV-03 | D6 | Critical Gate | 1.693% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-ENV-04 | D6 | Performance | 1.264% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-ENV-05 | D6 | Performance | 1.53% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-ENV-06 | D6 | Enhancement | 1.05% | Preliminary | Contextual only - insufficient to score | NOT LOCKED |  |  | N/A
V2-CON-01 | D7 | Mandatory | 1.327% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-CON-02 | D7 | Mandatory | 1.141% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-CON-03 | D7 | Critical Gate | 1.516% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-CON-04 | D7 | Performance | 1.215% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-CON-05 | D7 | Critical Gate | 1.739% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-CON-06 | D7 | Mandatory | 1.357% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-COM-01 | D7 | Mandatory | 1.473% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-COM-02 | D7 | Critical Gate | 1.672% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-OPS-01 | D7 | Mandatory | 1.468% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-OPS-02 | D7 | Mandatory | 1.202% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-OPS-03 | D8 | Performance | 0.7364% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-LIF-01 | D8 | Mandatory | 1.06% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-LIF-02 | D8 | Mandatory | 0.8914% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-LIF-03 | D8 | Mandatory | 0.952% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-LIF-04 | D8 | Mandatory | 1.059% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-LIF-05 | D8 | Performance | 0.9778% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-LIF-06 | D8 | Performance | 0.9247% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-LIF-07 | D8 | Performance | 0.7045% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-LIF-08 | D8 | Mandatory | 0.9487% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-LIF-09 | D8 | Performance | 0.8114% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-LIF-10 | D8 | Performance | 0.6219% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-DIG-01 | D9 | Mandatory | 0.6479% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-DIG-02 | D9 | Performance | 0.5854% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-DIG-03 | D9 | Enhancement | 0.4991% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-DIG-04 | D9 | Mandatory | 0.6029% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-DIG-05 | D9 | Mandatory | 0.684% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-GOV-01 | D9 | Critical Gate | 0.8398% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | NOT EVIDENCED
V2-GOV-02 | D9 | Mandatory | 0.7674% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-GOV-03 | D9 | Mandatory | 0.5645% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-GOV-04 | D9 | Mandatory | 0.634% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
V2-EVD-01 | D9 | Mandatory | 0.6947% | Not Evidenced | Not evidenced | NOT LOCKED |  |  | N/A
Note on A1: Source SHA-256: d9ec405927199dbbb635d6884491f71765606d3f0f3c36b0f1763ed3788f57b3

## SENSITIVITY_SCENARIOS
Evidence-Coverage Sensitivity and Evidence-Access Scenarios
These analyses vary weights or evidence availability only. They do not assign or simulate Mayo/Riyadh performance scores.
Domain_ID | Domain_Name | Locked_Domain_Weight | Context_Global_Weight | Within_Domain_Context_Coverage
D1 | Regulatory, Site & Access Governance
D2 | Spatial, Clinical & Women/Neonatal Planning
D3 | Vertical Transportation & Mobility Resilience
D4 | Fire & Life Safety
D5 | Critical MEP, Utilities & System Resilience
D6 | Environmental, Infection Control & Healing Environment
D7 | Constructability, Commissioning & Operational Readiness
D8 | Operations, Facilities & Lifecycle Performance
D9 | Digital Intelligence, Evidence & Governance
Locked-weight contextual coverage |  | Equal-domain-weight coverage
One-at-a-time domain-weight sensitivity
Scenario | Target_Domain | Perturbation | Locked_Domain_Weight | Within_Domain_Context | Renorm_Denominator | Perturbed_Context_Coverage | Delta_pp
D1_MINUS10 | D1 | -10%
D1_PLUS10 | D1 | 10%
D2_MINUS10 | D2 | -10%
D2_PLUS10 | D2 | 10%
D3_MINUS10 | D3 | -10%
D3_PLUS10 | D3 | 10%
D4_MINUS10 | D4 | -10%
D4_PLUS10 | D4 | 10%
D5_MINUS10 | D5 | -10%
D5_PLUS10 | D5 | 10%
D6_MINUS10 | D6 | -10%
D6_PLUS10 | D6 | 10%
D7_MINUS10 | D7 | -10%
D7_PLUS10 | D7 | 10%
D8_MINUS10 | D8 | -10%
D8_PLUS10 | D8 | 10%
D9_MINUS10 | D9 | -10%
D9_PLUS10 | D9 | 10%
D1_MINUS20 | D1 | -20%
D1_PLUS20 | D1 | 20%
D2_MINUS20 | D2 | -20%
D2_PLUS20 | D2 | 20%
D3_MINUS20 | D3 | -20%
D3_PLUS20 | D3 | 20%
D4_MINUS20 | D4 | -20%
D4_PLUS20 | D4 | 20%
D5_MINUS20 | D5 | -20%
D5_PLUS20 | D5 | 20%
D6_MINUS20 | D6 | -20%
D6_PLUS20 | D6 | 20%
D7_MINUS20 | D7 | -20%
D7_PLUS20 | D7 | 20%
D8_MINUS20 | D8 | -20%
D8_PLUS20 | D8 | 20%
D9_MINUS20 | D9 | -20%
D9_PLUS20 | D9 | 20%
OAT ±10% range
OAT ±20% range
Evidence-access scenarios (capacity only; no performance simulation)
Scenario | Evidence-access premise | Potential_Eligible_Indicators | Count_Coverage | Potential_Eligible_Locked_Weight | Critical_Gates_Resolved | Gate_Coverage | Complete_Project_HRWHPI
S0 — Current verified baseline | Current evidence rules; no indicator is final-score eligible. | [5 empty] | WITHHELD
S1 — Verify current contextual set | All currently contextual indicators become sufficient and benchmark-locked. | [5 empty] | WITHHELD
S2 — S1 + all Critical Gates | All Critical Gates become evidence-resolved, plus the contextual set. | [5 empty] | WITHHELD
S3 — S2 + all Mandatory | Critical Gate and Mandatory indicators become evidence-resolved, plus contextual Performance/Enhancement items. | [5 empty] | WITHHELD
S4 — Full evidence availability | All 72 indicators become evidence-resolved; no performance score is simulated. | [5 empty] | WITHHELD
Safeguard | Status
Scenarios quantify evidence availability, not project performance. | PASS
No missing Raw Score is converted to 0. | PASS
CAL-SIM is excluded from real-case evidence. | PASS
Complete-project HRWHPI remains withheld without authentic performance values. | PASS
Note on A1: Stage 8E source SHA-256: 6d62098912a1641b21901d8562f31531ff0be880d4baaa55b6d6f4d8ff00b8bb