Supplementary Information for

Reconciling calculation-based and measurement-based CO2 emissions: a full-year calibration study for carbon accounting management in a 1000 MW unit

Xi Penga, b,*, Junhong Zhoua, b,*, Wenjie Guoa, b, Zichen Huanga, b, Lichun Wangc, Yunbo Zhouc, Zhongjie Wua, b, Ping Donga, b, Weijun Zhangd, Ancheng Fanga, b, Guiqi Laia, b, Ling Chena, b, Cong-Qiang Liue

- a South China National Centre of Metrology/ Guangdong Institute of Metrology, Guangzhou, 510405, China

- b National Carbon Metrology Center (Guangdong), Guangzhou, 510405, China

- c Guoneng Qingyuan Power Generation Co., Ltd., Qingyuan, 511500, China

- d Guangdong Institute of Metrology, Dongguan Branch, Dongguan, 523000, China

- e Institute of Surface-Earth System Science, School of Earth System Science, Tianjin University, Tianjin, 300074, China

- *Corresponding author. All editorial communications during submission and revision will be handled by Xi Peng (pengxi5188@163.com)

- E-mail address: pengxi5188@163.com (X. Peng), johnzhou918@163.com (J. Zhou).

This file includes:

Number of pages: 6

Tables: S1-S9

Table S1 Evaluation of relative standard uncertainty via the calculation-based method

| Uncertainty component | Relative standard uncertainty (%) |
| --- | --- |
| Uncertainty from coal weighing process (uweighing) | 0.35 |
| Uncertainty due to representativeness of coal sampling (usampling) | 2.00 |
| Uncertainty from moisture measurement on as-received basis (umoisture1) | 0.42 |
| Uncertainty from moisture measurement on air-dried basis (umoisture2) | 0.42 |
| Uncertainty from elemental carbon content measurement on air-dried basis (ucarbon) | 0.70 |
| Uncertainty from using default values (udefault value) | 2.30 |
| Combined uncertainty (U) | 6.40 |

The total systematic uncertainty for each component is determined by applying a root sum square analysis to the coal weighing process, representativeness of coal sampling, moisture measurement on as-received basis, moisture measurement on air-dried basis, elemental carbon content measurement on air-dried basis, and using default values as follows:

| U= uweighing+usampling+umoisture1+umoisture2+ucarbon+udefault value | (S1) |
| --- | --- |

Table S2 Evaluation of relative standard uncertainty via the measurement-based method through comparison tests in March 2025

| Parameter | CEMS average value | Offset | Systematic Uncertainty |  |  | Combined standard uncertainty (%) | Combined relative standard uncertainty (%) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Comparison tests | Spatial | Instrumental |  |  |
| Velocity (100% load, m/s) | 18.53 | 1.59 | 0.16 | 0.13 | 1.02 | 1.04 | 5.60 |
| Velocity (55% load, m/s) | 11.99 | 0.86 | 0.15 | 0.11 | 0.67 | 0.69 | 5.78 |
| Velocity (32% –37% load, m/s) | 7.18 | 0.23 | 0.16 | 0.27 | 0.44 | 0.55 | 7.61 |
| CO2 concentration (99% load, %) | 16.37 | 1.12 | 0.17 | 0.13 | 0.09 | 0.23 | 1.41 |
| CO2 concentration (55% load, %) | 13.78 | 0.98 | 0.17 | 0.11 | 0.07 | 0.22 | 1.57 |
| CO2 concentration (32%~41% load, %) | 12.03 | 1.33 | 0.25 | 0.27 | 0.06 | 0.37 | 3.12 |

The combined relative standard uncertainty of CO2 emission derived from the measurement-based method (comparison tests in March 2025) under different operating conditions is determined by a root sum square analysis to the gas velocity, CO2 concentration uncertainties as follows:

| Uhigh= uhigh velocity+uhigh CO2 | (S2) |
| --- | --- |
| Umedium= umedium velocity+umedium CO2 | (S3) |
| Ulow= ulow velocity+ulow CO2 | (S4) |

Table S3 Combined relative standard uncertainty of CO2 emission derived from the measurement-based method (comparison tests in March 2025) under different operating conditions

| Operating conditions | Uncertainty component (%) |  | Combined relative standard uncertainty (%%, k=2) |
| --- | --- | --- | --- |
|  | Velocity | CO2 |  |
| High load (≥70% load) | 5.60 | 1.41 | 11.55 |
| Medium load (≥40%load, ≤70% load) | 5.78 | 1.57 | 11.98 |
| Low load (＜40% load) | 7.61 | 3.12 | 16.45 |

Using the results in Table S3, the overall uncertainty for the measurement-based method over January to June was obtained as a weighted average of the load-specific uncertainties, with weights equal to the hourly fractions of high, medium, and low load operation.

Table S4 Evaluation of relative standard uncertainty via the measurement-based method through comparison tests in September 2025

| Parameter | CEMS average value | Offset | Systematic Uncertainty |  |  | Combined standard uncertainty (%) | Combined relative standard uncertainty (%) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Comparison tests | Spatial | Instrumental |  |  |
| Velocity (100% load, m/s) | 20.47 | 1.54 | 0.15 | 0.13 | 1.14 | 1.15 | 5.63 |
| Velocity (51%–53% load, m/s) | 12.45 | 0.43 | 0.14 | 0.27 | 0.72 | 0.78 | 6.30 |
| CO2 concentration (99% load, %) | 15.96 | 1.16 | 0.26 | 0.13 | 0.09 | 0.30 | 1.89 |
| CO2 concentration (52%–54% load, %) | 14.21 | 0.89 | 0.18 | 0.27 | 0.08 | 0.34 | 2.38 |

Table S5 Combined relative standard uncertainty of CO2 emission derived from the measurement-based method (comparison tests in September 2025) under different operating conditions

| Operating conditions | Uncertainty component (%) |  | Combined relative standard uncertainty (%, k=2) |
| --- | --- | --- | --- |
|  | Velocity | CO2 |  |
| High load (≥70% load) | 5.63 | 1.89 | 11.88 |
| Medium and low load ( ≤70% load) | 6.30 | 2.38 | 13.47 |

Using the results in Table S5, the overall uncertainty for the measurement-based method over July to December was obtained as a weighted average of the load-specific uncertainties, with weights equal to the hourly fractions of high, medium, and low load operation.

Table S6 Combined relative standard uncertainty of CO2 emission derived from the calibrated measurement-based method (comparison tests in March 2025) under different operating conditions

| Parameter | CEMS average value | Offset | Systematic Uncertainty |  |  | Combined standard uncertainty (%) | Combined relative standard uncertainty(%) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Comparison tests | Spatial | Instrumental |  |  |
| Velocity (100% load, m/s) | 18.53 | 1.59 | 0.16 | 0.07 | 0.34 | 0.38 | 2.04 |
| Velocity (55% load, m/s) | 11.99 | 0.86 | 0.15 | 0.06 | 0.22 | 0.27 | 2.28 |
| Velocity (32%–37% load, m/s) | 7.18 | 0.23 | 0.16 | 0.15 | 0.15 | 0.26 | 3.68 |
| CO2 concentration (99% load, %) | 16.37 | 1.12 | 0.17 | 0.13 | 0.18 | 0.28 | 1.69 |
| CO2 concentration (55% load, %) | 13.78 | 0.98 | 0.17 | 0.11 | 0.15 | 0.25 | 1.82 |
| CO2 concentration (32%–41% load, %) | 12.03 | 1.33 | 0.25 | 0.27 | 0.12 | 0.39 | 3.24 |

Table S7 Combined relative standard uncertainty of CO2 emission derived from the calibrated measurement-based method (comparison tests in March 2025) under different operating conditions

| Operating conditions | Uncertainty component (%) |  | Combined relative standard uncertainty (%%, k=2) |
| --- | --- | --- | --- |
|  | Velocity | CO2 |  |
| High load (≥70% load) | 2.04 | 1.69 | 5.30 |
| Medium load (≥40%load, ≤70% load) | 2.28 | 1.82 | 5.84 |
| Low load (＜40% load) | 3.68 | 3.24 | 9.80 |

Using the results in Table S7, the overall uncertainty for the calibrated measurement-based method over January to June was obtained as a weighted average of the load-specific uncertainties, with weights equal to the hourly fractions of high, medium, and low load operation.

Table S8 Evaluation of relative standard uncertainty via the calibrated measurement-based method through comparison tests in September 2025

| Parameter | CEMS average value | Offset | Systematic Uncertainty |  |  | Combined standard uncertainty (%) | Combined relative standard uncertainty (%) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Comparison tests | Spatial | Instrumental |  |  |
| Velocity (100% load, m/s) | 20.47 | 1.54 | 0.15 | 0.12 | 0.37 | 0.42 | 2.05 |
| Velocity (51%–53% load, m/s) | 12.45 | 0.43 | 0.14 | 0.14 | 0.24 | 0.31 | 2.49 |
| CO2 concentration (99% load, %) | 15.96 | 1.16 | 0.26 | 0.05 | 0.17 | 0.32 | 1.97 |
| CO2 concentration (52%–54% load, %) | 14.21 | 0.89 | 0.18 | 0.02 | 0.15 | 0.24 | 1.67 |

Table S9 Combined relative standard uncertainty of CO2 emission derived from the measurement-based method (comparison tests in September 2025) under different operating conditions

| Operating conditions | Uncertainty component (%) |  | Combined relative standard uncertainty (%, k=2) |
| --- | --- | --- | --- |
|  | Velocity | CO2 |  |
| High load (≥70% load) | 2.05 | 1.97 | 5.69 |
| Medium and low load ( ≤70% load) | 2.49 | 1.67 | 6.01 |

Using the results in Table S9, the overall uncertainty for the calibrated measurement-based method over July to December was obtained as a weighted average of the load-specific uncertainties, with weights equal to the hourly fractions of high, medium, and low load operation.