Online Resources

Online Resource 1. Instrumentation and acquisition settings

| Quantity | Sensor / Instrument | Acquisition card | Measurement Range | Sampling Rate |
| --- | --- | --- | --- | --- |
| Manifold pressure Δp | PM20S piezoresistive pressure transducer | NI-9253 | 0–2 Bar | 1 Hz (from 1 kHz) |
| Blower D flow,QD. | FTM35 hot-wire anemometer | NI-9253 | 0–40 m/s | 1 Hz (from 1 kHz) |
| Blower D power,PD. | Three CT24B0100T02 current transformers (100:5) | NI-9244 (V) + NI-9227 (I) | 690 V rms L–L; 15–360 A pri. | 25 kHz, 19.5 s/min burst |

Table S1. Instrumentation and acquisition settings.

Online Resource 2. Measurement uncertainty budget

| Quantity | Instrument | Signal acquisition card | Accuracy (mfr.) | u (this study) |
| --- | --- | --- | --- | --- |
| Voltage | Direct (no switchboard PT) | NI-9244 | ±0.17% rdg (cal. max) | < 0.2% (≪ CT) |
| Current | CT24B0100T02 (100:5) | NI-9227 | ±3% (CT); ±0.37% (NI-9227) | ±3% (dominant) |
| Pressure | PM20S | NI-9253 | ±0.5% FS; ±0.41% (card) | ±0.5% FS (≈1 kPa) |
| Velocity | FTM35 hot-wire | NI-9253 | ±2%; ±0.41% (card) | ±2% rdg |

Table S2. Per-instrument measurement uncertainty budget.

Online Resource 3. Experimental sessions contributing to the directional sensitivity analysis

| Session | Config | Single-blower events |
| --- | --- | --- |
| 4 | ACD | C: −10%(×3), +20%(×3); A: +20%(×3) |
| 6 | ACD | A: −10% (×2), +20%(×1) |
| 5 & 6 | BCD | C: −10% (×2), +20%(×2); B: −10%(×1), +20%(×3) |

Table S3. Experimental sessions contributing to Section 4.

Online Resource 4. Cross-validation test results

| Test | ACD result | BCD result |
| --- | --- | --- |
| Test 1: Pressure–power correlation | r = 0.67, p = 0.009, R² = 45% | r = 0.53, p = 0.078, R² = 28% |
| Test 2: Partial correlation controlling Blower D flow | partial r = 0.44, p = 0.11, partial r² = 19% | partial r = −0.04, p = 0.89, partial r² = 0.2% |
| Test 3: Implied aerodynamic efficiency | Two-sided Mann–Whitney U = 87, p = 0.90 (N = 14 vs 12) mean Π_op = 2.19, CV = 5.9%, N = 14 | mean Π_op = 2.16, CV = 10.1%, N = 12 |

Table S4. Cross-validation tests results.