Energy reduction with application of Shaft in Water Supply Systems

Anujkumar Ghorpade1, Abhishek Kumar Sinha2, Pradip Kalbar3

1Ph.D. Student, Centre for Urban Science and Engineering, Indian Institute of Technology Bombay, Powai, Mumbai, 400076, India. Email: anuj_32@iitb.ac.in

2Ph.D. Student, Centre for Urban Science and Engineering, Indian Institute of Technology Bombay, Powai, Mumbai, 400076, India. Email: aksinha.cuse@iitb.ac.in

3Assistant Professor, Centre for Urban Science and Engineering, Indian Institute of Technology Bombay, Powai, Mumbai, 400076, India (corresponding author). Email: kalbar@iitb.ac.in

Fig. S1: Location of case studies

- Theory of Bernoulli’s theorem

Energies per unit weight of the fluid

Pressure energy= Pρg

Kinetic energy= v22g

Datum energy=z

Mathematically, the Bernoulli’s theorem is written as,

Pρg+v22g+z=constant                                                              (1)

(1)

(2)

z1

z2

P1ρg

P2ρg

v122g

v222g

hL

Hydraulic Grade Line

Total Energy Line

Fig. S2: Total Energy Line (TEL) and Hydraulic Grade Line (HGL) for real fluid moving from point (1) to (2).

- Mathematical formulations for determination of operational energy

P=Q*H*g*ρPump efficiency                                                          (2)

Where, Q is discharge in m3/sec, and H is pump head in meter.

hf=10.7 LC1.85d4.87Q1.85                                                              (3)

Where, L in length of pipe in meter, d is diameter in meter, Q is discharge in m3/sec, and C is Hazen Williams coefficient of roughness.

SEC= EpQv                                                                                  (4)

Where, Ep in pump energy in kWh, and Qv is discharge volume in m3.

Pinf=1+wn-1w1+wn                                                      (5)

Where,

w=1+ir1+if-1                                                                 (6)

Where,

ir is rate of interest on capital investment, which is considered as 10% per annum.

if is rate of inflation for replacement cost, which is considered as 6% per annum.

n is design period, which is considered as 30 years.

Unit rate of power is considered as 0.067 USD/unit.

A

A1+if

A1+if2

A1+if3

A1+ifn

Pinf

1

3

2

4

N

.           .             .              .           .

Fig. S3: Cash flow diagram for present worth calculation with inflation rate

- Site visit to the study area

| (a) | (b) |
| --- | --- |

Fig. S4: Shaft at Bhima river WSS, Solapur, Maharashtra. (a) Old shaft (before 1984), (b) New shaft (post 2015).

| (a) | (c) |
| --- | --- |
| (b) | (d) |

Fig. S5: Shaft at Pise weir WSS, Thane, Maharashtra. (a)- Pise weir, (b)- Pump house, (c)- Old Shaft and (d)- New shaft.

(a)

(b)

Fig. S6: Schematic of transmission network between pump house to WTP of Pise weir WSS, Thane, Maharashtra, India. (a) From 1998 to 2009, and (b) From 2009 onwards.

Exchange rate of currency 1 INR=0.013 USD on 24th July 2021