## Data_from_SWM
Personal communication via eMail

Date:	26.02.2018
Correspondent:	Christian Pletl		pletl.christian@swm.de
	Leitung Dezentrale Erzeugung und Erneuerbare Energien regional
	SWM – Stadtwerke München

Geothermal site	electr. output	therm. / output / (current)	therm. / output / (planned)	production / rate	production well-head / temperature	injection well-head / temperature	ESP power consumption
Geothermieanlage	elektr. Leistung in MW	therm. Leistung in MW aktuell	therm. Leistung in MW geplant	Förderrate in l/s	Fördertemp. in °C	Injektions-temp. in °C	TKP Leistungs-aufnahme in kW
Riem	-	13	-	85	95	55	500
Freiham	-	13	25	110	89	60	735
Sauerlach	5	4	-	110	140	38 bis 48	1200
Dürrnhaar	6	-	10	135	138	40 bis 50	1350
Kirchstockach	6	-	10	135	130	40 bis 50	1000

## Data_and_Calculation
Site	case	Political region	Geological region	east	north	Latitude	Longitude	Link to	Rock layer	Reservoir	zres	zwl	Production rate V̇		ṁ	Gas-Liquid-Ratio	Pth,out	Pel,brutto	ηel	Pth,in	Pel,ORC	Pel,aux	Pel,netto	WHTprod	WHTinj	WHPprod	ρ	cp	Pth,well,cp	Δh	Pth,well,Δh	PI (Productivity index)			pESP,in	pESP,out	PESP,hyd	ηpump	PESP,rot	ηmotor	PESP,el	ηcable	ηtrafo	ηVSD	ηprod,tot	Pprod,el	II (Injectivity index)			pinj,in	pinj,out	Pinj,hyd	Pinj,rot	ηinj,tot	Pinj,el	Pcirc,el	Pel,in,brineLoop	ε	εΔh	Quality	COPCarnot	εreal/COP	T_m	Quality	Exergy flow	ζFlow	ζCarnot	ζFlow/ζCarnot	ζFlow
	White cells = input, gray cells = calculated			[m]	[m]			Google Maps		type	m	m	m³/h	l/s	kg/s		MWth	MWel		MWth	MWel	MWel	MWel	°C	°C	bar	kg/m³	J/kg/K	MWth	J/kg	MWth	l/s/bar	m³/h/MPa	m³/s/Pa	bar	bar	MWmech		MWmech		MWel					MWel	l/s/bar	m³/h/MPa	m³/s/Pa	bar	bar	MWmech	MWmech		MWel		MWel			for T_wh, 0 °C			°C	for T_m, 0 °C		for 0 °C			for 20 °C
Neustadt-Glewe		NE Germany	North-German Basin	3672199	5918488	53.370119	11.586183	show		hydro			103.7	28.8	32.3		2.6	0.23	9%					96	71.3		1122	3361	2.7				300.0	8.3E-08												0.163		180	5.0E-08								0.163	16		0.26	3.8	4.3	84	0.23	0.63	3.9	0.9	4.3	2.9
Neustadt-Glewe (GeotIS)		NE Germany	North-German Basin							hydro				35.0										97					4																												0.163			0.26	-	-		-	-	-	-		-
Groß Schönebeck	real	NE Germany	North-German Basin	3809607	5873404	52.903859	13.601582	show	Rotliegend	hydro	-4389		15	4.1	4.7									99	60		1136	3287	0.6			0.4	15.0	4.2E-09												0.099	0.1	4	1.1E-09						0.043		0.142	4		0.27	3.8	1.1	79	0.22	0.14	1.0	0.8	1.1	0.7
Groß Schönebeck	expected	NE Germany	North-German Basin							hydro	-4389		15	4.1	4.6									140	60		1111	3312.5	1.2			0.4	15.0	4.2E-09												0.099	0.1	4	1.1E-09						0.043		0.142	9		0.34	3.0	2.9	99	0.27	0.32	2.3	0.8	2.9	1.8
Traunreut		Bavaria	South-German Basin	3767319	5321196	47.973038	12.579515	show	Malm	hydro			524	143.3			8.8	3.3	13%	25.2	0.55	1.9	1.4	114	57.9				34.0						34	80	0.6693								51%	1.308				8.9	13.86	0.07		51%	0.14		1.450	23		0.29	3.4	6.9	85	0.24	8.08	5.6	0.8	6.9	4.3
Traunreut		Bavaria	South-German Basin			47.973038	12.579515	show	Malm	hydro				145.5	138.0									114	57.2		948	4201	32.7	238639	32.9															1.308									0.14		1.450	23		0.29	3.4	6.6	85	0.24	7.75	5.3	0.8	6.6	4.1
Unterhaching		Bavaria	South-German Basin						Malm	hydro			540	150.0			38	3.36	13%	25.5				123					63.5																	1.471							0		0.000		1.471	43		0.31	-	-	-	-	-	-	-		-
Unterhaching		Bavaria	South-German Basin			48.057078	11.597516	show	Malm	hydro				140.0	131.7			3.36						123.3	59		941	4206	35.5																	1.65							0		0.000		1.650	21		0.31	3.2	6.7	90	0.25	8.82	5.3	0.8	6.7	4.2
Unterhaching		Bavaria	South-German Basin	3693695	5327601	48.057078	11.597516	show	Malm	hydro			540	150.0										122	60				38.0																	1.320									0.000		1.320	29		0.31	3.2	8.9	90	0.25	9.43	7.1	0.8	8.9	5.6
Laufzorn/Oberhaching		Bavaria	South-German Basin	3691252	5323391	48.019989	11.562898	show	Malm	hydro	-3,320…-3,755		576	160.0				3.5						125					40																	1.350											1.350	30		0.31	-	-	-	-	-	-	-		-
Laufzorn/Oberhaching		Bavaria	South-German Basin						Malm	hydro			324	90.0			40	4.3						127	60				40.0																	0.759											0.759	53		0.32	3.2	16.7	92	0.25	10.12	13.3	0.8	16.7	10.4
Laufzorn/Oberhaching		Bavaria	South-German Basin	?		48.0200584	11.5626777	show	Malm	hydro	-4083		504	140.0	130.9		40	4.3						128	50		935	4209	40.0																	1.300									0		1.300	31		0.32	3.1	9.8	88	0.24	9.71	7.5			5.8
Riem		Bavaria	South-German Basin	3702231	5336536	48.134699	11.716129	show	Malm	hydro			306	85.0	81.8		13							95	55		962	4191	13.7	167638	13.7															0.500									0		0.500	27	27	0.26	3.9	7.1	75	0.21	2.94	5.9	0.8	7.1	4.3
Freiham		Bavaria	South-German Basin	3679072	5336189	48.138512	11.405124	show	Malm	hydro			396	110.0	106.3		13							89	60		966	4190	12.9	121508	12.9															0.735									0		0.735	18	18	0.25	4.1	4.3	74	0.21	2.76	3.8	0.9	4.3	2.7
Sauerlach	best	Bavaria	South-German Basin	3699334	5318411	47.972782	11.668815	show	Malm	hydro	-4757…-5567		396	110.0	101.9		4	5						140	38		926	4211	43.8	429546	43.8															1.200									0		1.200	36	36	0.34	3.0	12.4	87	0.24	10.54	8.8	0.7	12.4	6.8
Sauerlach	worst	Bavaria	South-German Basin						Malm	hydro			396	110.0	101.9		4	5						140	48		926	4215	39.5	387781	39.5															1.200									0		1.200	33	33	0.34	3.0	11.2	92	0.25	9.96	8.3	0.7	11.2	6.5
Dürrnhaar	best	Bavaria	South-German Basin	3703522	5321170	47.996251	11.726149	show	Malm	hydro			486	135.0	125.3			6						138	40		928	4211	51.7	412630	51.7															1.350									0		1.350	38	38	0.34	3.0	12.9	87	0.24	12.47	9.2	0.7	12.9	7.1
Dürrnhaar	worst	Bavaria	South-German Basin						Malm	hydro			486	135.0	125.3			6						138	50		928	4214	46.5	370862	46.5															1.350									0		1.350	34	34	0.34	3.0	11.6	92	0.25	11.73	8.7	0.8	11.6	6.8
Kirchstockach	best	Bavaria	South-German Basin	3700546	5324490	48.027016	11.687868	show	Malm	hydro			486	135.0	126.3			6						130	40		935	4205	47.8	378461	47.8															1.000									0		1.000	48	48	0.32	3.1	15.4	83	0.23	11.15	11.1	0.7	15.4	8.5
Kirchstockach	worst	Bavaria	South-German Basin						Malm	hydro			486	135.0	126.3			6						130	50		935	4209	42.5	336694	42.5															1.000									0		1.000	43	43	0.32	3.1	13.7	89	0.24	10.40	10.4	0.8	13.7	8.1
Bruchsal		Pfalz	Rhinegraben	3468500	5443260	49.125719	8.567375	show	Buntsandstein	hydro			86.4	24.0	25.0	2,2 l CO2 je Kilogramm Thermalwasser unter Normbedingungen		0.55						125.9	66.8	2.16			5.4																	0.133									0		0.133	41	0	0.32	3.2	12.9	96	0.26	1.41	10.6	0.8	12.9	8.4
Landau		Pfalz	Rhinegraben	3436000	5450000	49.18379	8.12106	show	Buntsandstein	hydro	2391		252	70	68.7		5	0.79						159	50		982	3837	28.7	461274	31.7															0.448											0.448	64		0.37	2.7	23.6	102	0.27	7.81	17.4	0.7	23.6	14.0
Landau		Pfalz	Rhinegraben			49.18379	8.12106	show					144	40				3						159					33																	0.256											0.256	129		0.37	-	-	-	-	-	-	-		-
Landau		Pfalz	Rhinegraben			49.18379	8.12106	show					252	70	68.7		5	3						160	50		982	3837	29.0																	0.600									0		0.600	48				-	102	0.27	7.90	13.2			10.6
Insheim		Pfalz	Rhinegraben	3438310	5446618	49.15362	8.153262	show	Basement	hydro			306	85	83.5			4.8				1.2		165	46		982	3837	38.0																	0.544											0.544	70		0.38	2.7	26.3	103	0.27	10.37	19.1	0.7	26.3	15.4
Insheim		Pfalz	Rhinegraben			49.15362	8.153262	show					288	80	78.5			4.8						165	70		982	3837	28.6																	0.8									0		0.800	36		0.38		-	116	0.30	8.51	10.6	0.8	13.5	8.8
Südpfalz		Pfalz	Rhinegraben																			0.75		165					45.0																												0.750	60		0.38	-	-	-	-	-	-	-		-
Soultz-sous-Forêts	best	Alsace/France	Rhinegraben			48.930896	7.866805	show		petro	-5000		110	31	30	1.03		1.7			1.7	0.6	1.1	150	70	23	983	3907	9.4			0.8	28.8	8E-09	1	39.2	0.12								70%	0.166	0.8		8.0E-09	1.0	39.2	0.11			0.000		0.166	56		0.35	2.8	20.0	109	0.28	2.67	16.0	0.8	20.0	13.1
Rittershoffen		Alsace/France	Rhinegraben			48.8965196	7.9386272	show		hydro	-2700		260	72	70	1.2	24	0						170	80	25	968	3915	24.7			3.5			1	21.7	0.15									0.213	2.5								0.000		0.213	116		0.38	2.6	44.3	123	0.31	7.67	36.0	0.8	44.3	30.1
Rittershoffen													279	77	75									170	80		968	3915	26.4			2.8			1	28.7	0.21									0.306	2.5								0.000		0.306	86		0.38	2.6	33.1	123	0.31	8.22	26.8	0.8	33.1	22.5
Klaipeda		Lithuania	Baltic Basin			55.74833333	21.20222222	show	Sedimentary, Sandstone	hydro			201…539	78…103	82…108									38	16		1053	3844	6.9…9.2																	0.276…0.422									0.288			12…13	0…0	0.12…0.12	8.19…8.19	-		0.09…0.09		0.90…1.20	0.73…0.73	1.49…1.63	0.23…0.50
Klaipeda	best	Lithuania	Baltic Basin						Sedimentary, Sandstone	hydro		-9	539	149.85	157.95		17							39	11	14	1054	3844	17.0			65.2		7E-07	12.7	15.0	0.034								70%	0.049	6.5		6.5E-08	14	37	0.34		70%	0.492		0.542	31				-	25	0.083	1.41	2.61			0.50
Klaipeda		Lithuania	Baltic Basin						Sedimentary, Sandstone	hydro			201	55.83	58.82									38	16		1053	3844	5.0						17.25	45.96	0.160				0.188				58%	0.2762						0.153		69%	0.221		0.498	10		0.12	8.2	1.2	27	0.090	0.45	0.90	0.73	1.2	0.23
Klaipeda		Lithuania	Baltic Basin						Sedimentary, Sandstone	hydro			200…350																								0.160															0.049		73%	0.067		0.067			0.00	-	-	-		-		-		-
Klaipeda	Case 1	Lithuania	Baltic Basin						Sedimentary, Sandstone	hydro			350	97.2	102.4									38	16		1053	3844	8.7						17.25	45.7	0.277	85%	0.325	88%	0.370	99%	98%	98%	71%	0.391	0.37					0.202			0.288		0.679	13		0.12	8.2	1.6	27	0.090	0.78	1.14	0.7	1.6	0.29
Klaipeda	Case 2	Lithuania	Baltic Basin						Sedimentary, Sandstone	hydro			370	102.8	108.3									38	16		1053	3844	9.2						17.25	44.2	0.277	84%	0.329	88%	0.376	99%	98%	98%	70%	0.397						0.202			0.288		0.685	13		0.12	8.2	1.6	27	0.090	0.82	1.20	0.7	1.6	0.31
Klaipeda	Case 3	Lithuania	Baltic Basin						Sedimentary, Sandstone	hydro			280	77.8	81.9									38	16		1053	3844	6.9						17.25	42.6	0.197	85%	0.233	87%	0.266	99%	98%	98%	70%	0.281						0.202			0.288		0.569	12		0.12	8.2	1.5	27	0.090	0.62	1.09	0.7	1.5	0.28
Klaipeda	Case 4	Lithuania	Baltic Basin						Sedimentary, Sandstone	hydro			350	97.2	102.4									38	16		1053	3844	8.7						17.25	47.3	0.292	85%	0.343	86%	0.399	99%	98%	98%	69%	0.422						0.202			0.288		0.710	12		0.12	8.2	1.5	27	0.090	0.78	1.09	0.7	1.5	0.28
Klaipeda	log	Lithuania	Baltic Basin						Sedimentary, Sandstone	hydro			210…280																																												0.000				-	-	-		-				-
Mezőberény		Hungary	Pannonian Basin			46.8265059	21.0258852	show		hydro				8.3…8.3										80	50		975	4177.3	1.0…1.0												0.008					0.020									0.005		0.025	48…45			4.4…4.4	-				6.9…9.2	0.8…0.8	8.2…10.9	4.8…6.4
Mezőberény	summer	Hungary	Pannonian Basin							hydro			30	8.3	8.1									80	50		975	4177.3	1.0																	0.013									0.013		0.027	38		0.23	4.4	8.7	65	0.19	0.20	7.3	0.8	8.7	5.1
Mezőberény	winter	Hungary	Pannonian Basin							hydro			46	12.8	12.5									80	50		975	4177.3	1.6																	0.023									0.018		0.041	39		0.23	4.4	8.7	65	0.19	0.30	7.4	0.8	8.7	5.1
Mezőberény	summer	Hungary	Pannonian Basin							hydro			30	8.3	8.1									80	50		975	4177.3	1.0												0.006					0.013									0.008	0.008	0.021	48		0.23	4.4	10.9	65	0.19	0.20	9.2	0.8	10.9	6.4
Mezőberény	winter	Hungary	Pannonian Basin							hydro			46	12.8	12.5									80	50		975	4177.3	1.6												0.011					0.023									0.012	0.012	0.035	45		0.23	4.4	10.1	65	0.19	0.30	8.6	0.8	10.1	5.9
Mezőberény	summer	Hungary	Pannonian Basin							hydro	-1700		30	8.3	8.1									80	50		975	4177.3	1.0			1.2	43.038	1.1955E-08	0	7.0	0.006				0.008				0.7	0.020	2.0	71.1	1.975E-08	7.5	11.7	0.004		70%	0.005	0.005	0.025	40		0.23	4.4	9.1	65	0.19	0.20	7.7	0.8	9.1	5.3
Mezőberény	winter	Hungary	Pannonian Basin							hydro			46	12.8	12.5									80	50		975	4177.3	1.6			1.2	43.038	1.1955E-08	0	10.7	0.014				0.020				0.7	0.032	2.0	71.1	1.975E-08	8.5	15.0	0.008		70%	0.012	0.007	0.043	36		0.23	4.4	8.2	65	0.19	0.30	6.9	0.8	8.2	4.8
Generic best case											-2000	-100	184	51	51.2									150	45	10	1000	4000	21.5			2.78E-01	10.0	2.8E-09	2.0	206.3	1.046								70%	1.494	2.78E-01	10.0	2.8E-09	10	175.5197	0.85		70%	1.211		2.705	7.9		0.35	2.8	2.8	95	0.258	5.55	2.05	0.7	2.8	1.62

## Export
Reduced version of the table for export to article

Site	case	Political region	Geological region	zres	east	north	Latitude	Longitude	Rock layer	Reservoir	Pth,out	Pel,brutto	ηel	Pth,in	WHTprod	WHTinj	WHPprod	cp	ρ	#BEZUG!	Production rate V̇	0	ṁ	Pth,well,cp	Δh	Pth,well,Δh	PI (Productivity index)	0	0	pESP,in	pESP,out	PESP,hyd	PESP,rot	ηVSD	ηprod,tot	PESP,el	Pcirc,el		Pprod,el	#BEZUG!	ηprod,tot	ηVSD	pinj,in	pinj,out	Pinj,hyd	Pinj,rot			Pinj,el	ηinj,tot	Pel,ORC	Pel,aux	Pel,netto	ε	εΔh	#BEZUG!	COPCarnot	Quality	#BEZUG!	T_m	Quality	Exergy flow	ζFlow	ζFlow	ζFlow/ζCarnot	Latitude	Longitude
	White cells = input, gray cells = calculated				[m]	[m]				type	MWth	MWel		MWth	°C	°C	bar	J/kg/K	kg/m³	#BEZUG!	m³/h	l/s	kg/s	MWth	J/kg	MWth	l/s/bar	m³/h/MPa	m³/s/Pa	bar	bar	MWmech	MWmech			MWel			MWel	#BEZUG!	l/s/bar	m³/h/MPa	m³/s/Pa	bar	bar	MWmech	MWmech		MWel	MWel	MWel	MWel	MWel			#BEZUG!	for T_wh, 0 °C	0	#BEZUG!	°C	0		0 °C	20 °C
Neustadt-Glewe		NE Germany	North-German Basin					2.6	0.23	0.088461538		97	71.3		3361	1121.936596	103.7		29	32.31800696	4					0.163	#BEZUG!					16		#BEZUG!	3.8					3.9	2.9	0.9	53.370119	11.586183
Traunreut		Bavaria	South-German Basin					8.8	3.32537734	0.13186	25.219	113.69	57.888673				523.8		143		34.019	34	80	0.6693					1.308	#BEZUG!	0.511697248		8.9	13.86	0.072168				0.14187	0.508691055	0.55	1.930168	1.39520934	23		#BEZUG!	3.4					5.6	4.3	0.8
Groß Schönebeck		NE Germany	North-German Basin					99	60		3287	1136	14.89		4	4.696802333	0.6					0.099	#BEZUG!					0.043089112					4		#BEZUG!	3.8					1.0	0.7	0.8	52.903859	13.601582
Groß Schönebeck		NE Germany	North-German Basin					140	60		3313	1111	14.89		4	4.595219444	1.2					0.099	#BEZUG!					0.043089112					9		#BEZUG!	3.0					2.3	1.8	0.8
Unterhaching		Bavaria	South-German Basin					38	3.36	0.13186	25.48157136	123					540		150		63.5					1.471	#BEZUG!					0			0					43		#BEZUG!	-					-	-	-	47.973038	12.579515
Unterhaching		Bavaria	South-German Basin					3.36			123.3	59.28131794		4206	941			140	131.7143741	35.5					1.650	#BEZUG!					0			0					21		#BEZUG!	3.2					5.3	4.2	0.8	47.973038	12.579515
Laufzorn/Oberhaching		Bavaria	South-German Basin					3.5			125					576		160		40.0					1.350	#BEZUG!					30		#BEZUG!	-					-	-	-
Dürrnhaar		Bavaria	South-German Basin					6			138	40…50	#BEZUG!	4211…4214	928	#BEZUG!	486	135	125.3150789	46…52	370862…412630	46…52					1.350	#BEZUG!					0	#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!	34…38	34…38	#BEZUG!	3.0	0	#BEZUG!	87…92	0…0	12…12	8.7…9.2	6.8…7.1	0.7…0.8	47.996251	11.726149
Freiham		Bavaria	South-German Basin					13				89	60		4190	966	396		110	106.3037875	12.9					0.735	#BEZUG!					0					18		#BEZUG!	4.1					3.8	2.7	0.9	48.138512	11.405124
Laufzorn/Oberhaching		Bavaria	South-German Basin					40	4.3			127	60				324		90		40.0					0.759	#BEZUG!					53		#BEZUG!	3.2					13.3	10.4	0.8	47.972782	11.668815

Kirchstockach			South-German Basin					130	40…50	#BEZUG!	4205…4209	935	#BEZUG!	486	135	126.2534534	43…48	336694…378461	43…48					1.000	#BEZUG!					0	#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!	43…48	43…48	#BEZUG!	3.1	0	#BEZUG!	83…89	0…0	10…11	10.4…11.1	8.1…8.5	0.7…0.8	48.027016	11.687868
Riem		Bavaria	South-German Basin					13				95	55		4191	962	306		85	81.79636193	13.7					0.500	#BEZUG!					0					27		#BEZUG!	3.9					5.9	4.3	0.8	48.134699	11.716129
Sauerlach		Bavaria	South-German Basin					4	5			140	38…48		4211…4215	926	#BEZUG!	396	110	102	40…44	387781…429546	40…44					1.200	#BEZUG!					0	#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!	33…36	33…36	#BEZUG!	3.0	0	#BEZUG!	87…92	0…0	10…11	8.3…8.8	6.5…6.8	0.7…0.7	47.972782	11.405124

Dürrnhaar
Kirchstockach		Bavaria	South-German Basin					6
Laufzorn/Oberhaching			South-German Basin					128	50		4209	935	504		140	130.9295072	40.0					1.300	#BEZUG!					0					31		#BEZUG!	3.1					7.5	5.8		48.0200584	11.5626777
Traunreut		Bavaria	South-German Basin					113.7	57.2		4201	948			146	137.9737625	32.7					1.308	#BEZUG!					0.142					23		#BEZUG!	3.4					5.3	4.1	0.8	47.973038	12.579515
Unterhaching		Bavaria	South-German Basin					3.36			123.3	59		4206	941			140	131.7143741	35.5					1.650	#BEZUG!					0			0					21		#BEZUG!	3.2					5.3	4.2	0.8	48.057078	11.597516
Unterhaching		Bavaria	South-German Basin					122	60		4206	941	540		150		38.0					1.320	#BEZUG!					0					29		#BEZUG!	3.2					7.1	5.6	0.8	48.057078	11.597516
Bruchsal			Rhinegraben					126	66.8				86.4		24	25	5.4					0.133	#BEZUG!					0					41		#BEZUG!	3.2					10.6	8.4	0.8	49.125719	8.567375
Insheim		Pfalz	Rhinegraben					4.8			165	70		3837	982	288		80	78.54847789	28.6					0.800	#BEZUG!					0					36		#BEZUG!					10.6	8.8	0.8	49.15362	8.153262
Landau		Pfalz	Rhinegraben					5	3			160	50		3837	982	252		70	68.72991816	29.0					0.600	#BEZUG!					0					48		#BEZUG!					13.2	10.6		49.18379	8.12106
Landau					49.15362	8.153262
Südpfalz					49.15362	8.153262
Rittershoffen			Rhinegraben					24…24	0			170	80	#BEZUG!	3915	968	#BEZUG!	260…279	72…77	75	25…26			3…4			1	22…29	0…0					0.213…0.306	#BEZUG!	3					0	#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!	86…116		#BEZUG!	2.6	0	#BEZUG!	123	0	8…8	26.8…36.0	22.5…30.1	1	48.8965196	7.9386272
Soultz-sous-Forêts		Alsace/France	Rhinegraben					#BEZUG!			150	70		3907	983	109.8806609		31	30	9.4	1	39.15300725	0.116452157					0.166	#BEZUG!	0.7		1	39.15300725	0.114459022				0		1.7	0.6	1.1	56		#BEZUG!	2.8					16.0	13.1	0.8	48.930896	7.866805
					48.8965196	7.9386272
Klaipeda		Lithuania	Baltic Basin					0…0				38	16		3844	1053	#BEZUG!	280…370	78…103	82…108	6.9…9.2					0.281…0.422	#BEZUG!					0.288					12…13	0…0	#BEZUG!	8…8	0…0	#BEZUG!		0…0		1.09…1.20	0.28…0.31	0.73…0.73	55.74833333	21.20222222
Klaipeda		Lithuania	Baltic Basin					38…38	16…16		3844…3844	1053…1053	#BEZUG!	280…370	78…103	82…108	6.9…9.2					17…17	43…47	0			1…1	0…0			0.281…0.422	#BEZUG!					0.202…0.202		0.000…0.000	0.288…0.288	0…1				12…13		#BEZUG!	8…8	0…0	#BEZUG!	27…27	0…0	1…1	1.09…1.20	0.28…0.31	0.73…0.73
Klaipeda		Lithuania	Baltic Basin					#BEZUG!	280…350					0…0					#BEZUG!					0.202…0.202		0.000…0.000	0.005…0.288	0…1					#BEZUG!	8…8	0…0	#BEZUG!	27…27		1…1		0.28…0.28	0.73…0.73
Klaipeda		Lithuania	Baltic Basin					38	16		3844	1053	#BEZUG!	30…350	8…97	8…102	1.0…8.7					17	47…47	0	0…0	1	1…1	0…0			0.013…0.422	#BEZUG!	0.000…0.000					0			0	0…1				12…38		#BEZUG!	8.2	0	#BEZUG!	27	0	0…1	1.09…7.32	0.28…5.06	1
Klaipeda		Lithuania	Baltic Basin					38	16		3844	1053	#BEZUG!	30…46	8…13	8…12	1.0…1.6					17	0…0	0…0	0…0	1	0…0	0…0			0.013…0.023	#BEZUG!					0			0	0…0				38…39		#BEZUG!	8.2	0	#BEZUG!	27	0	0…0	7.32…7.39	5.06…5.11	1
Klaipeda		Lithuania	Baltic Basin					38	16		3844	1053	#BEZUG!	30…46	8…13	8…12	1.0…1.6					17	0…0	0…0	0…0	1	0…0	0…0			0.013…0.023	#BEZUG!					0			0	0…0				38…48		#BEZUG!	8.2	0	#BEZUG!	27	0	0…0	7.32…9.23	5.06…6.38	1
Klaipeda		Lithuania	Baltic Basin					80…80	50…50		4177…4177	975…975	#BEZUG!	30…46	8…13	8…12	1.0…1.6					0…0	0…0	0…0	0…0	0…0	0…0	0…0			0.013…0.023	#BEZUG!					0.000…0.000			0.008…0.018	0…0				38…48		#BEZUG!	4…4	0…0	#BEZUG!	65…65	0…0	0…0	7.32…9.23	5.06…6.38	0.85…0.85
Klaipeda		Lithuania	Baltic Basin					#BEZUG!	30…46					#BEZUG!					0…0					#BEZUG!	4…4		#BEZUG!	65…65		0…0		5.11…6.38
Mezőberény		Hungary	Pannonian Basin					80	50		4177	975	#BEZUG!		8.3…12.8		1.0…1.6					0…0			0.013…0.032	#BEZUG!					0.005…0.012	0…0				36…48		#BEZUG!	4…4		#BEZUG!				6.9…9.2	4.8…6.4	0.8…0.8	46.8265059	21.0258852
#BEZUG!					80	50		4177	975	#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!					#BEZUG!	#BEZUG!					#BEZUG!	#BEZUG!				#BEZUG!				0	#BEZUG!	65	0	#BEZUG!	#BEZUG!		#BEZUG!
Generic best case					80	50		4177	975	#BEZUG!	30…184	8…51	8…51	1.0…21.5					0.020…1.494	#BEZUG!					0.005…1.211	0…3				8…40				0	#BEZUG!	65	0	0…6	2.05…7.71		8.3…51.2

## Variation
Parameter variation for a generic geothermal heat plant

	WHTprod	150	°C
	WHTinj	70	°C				net exergy maximum		3.106	MW
	WHPprod	10	bar
	PI	0.15	l/s/bar	5.4	m³/h/MPa			at	70	kg/s
	II	0.15	l/s/bar	5.4	m³/h/MPa
	ρ	1000	kg/m³
	cp	4000	J/kg/K
	ηpump,tot	0.7
	T0	0	°C

Variation of production rate for the Soultz-sous-Forêts site using Excel Data Table
	ṁ / [kg/s] (production rate)	Pth,out	ΔpESP	PESP,hyd	Δpinj	Pinj,hyd	Pel,brineLoop	Tm	Exergy flow	net exergy output	ε (energy conversion factor)	ζ (exergy conversion factor)
	[kg/s]	MWtherm	bar	MWmech	bar	MWmech	MWel	°C	MWex	MWex
	10	3.2	67	0.1	67	0.1	0.2	109	0.9	0.8	16.8	4.8		Upper limit of ṁ axis
	11	3.5	73	0.1	73	0.1	0.2	109	1.0	0.9	15.3	4.3		125
	13	4.2	87	0.1	87	0.1	0.3	109	1.2	1.1	12.9	3.7	𝑄̇out / [MW] (thermal output) / conversion factor / E*out , Pel,in, / [MW]
	15	4.8	100	0.2	100	0.2	0.4	109	1.4	1.2	11.2	3.2
	20	6.4	133	0.3	133	0.3	0.8	109	1.8	1.6	8.4	2.4
	25	8.0	167	0.4	167	0.4	1.2	109	2.3	1.9	6.7	1.9
	30	9.6	200	0.6	200	0.6	1.7	109	2.7	2.1	5.6	1.6
	35	11.2	233	0.8	233	0.8	2.3	109	3.2	2.4	4.8	1.4
	40	12.8	267	1.1	267	1.1	3.0	109	3.6	2.6	4.2	1.2
-7.96884%	45	14.4	300	1.4	300	1.4	3.9	109	4.1	2.7	3.7	1.1
-4.80091%	50	16.0	333	1.7	333	1.7	4.8	109	4.6	2.9	3.4	1.0
	55	17.6	367	2.0	367	2.0	5.8	109	5.0	3.0	3.1	0.9
3.64556%	60	19.2	400	2.4	400	2.4	6.9	109	5.5	3.1	2.8	0.8
6.13577%	70	22.4	467	3.3	467	3.3	9.3	109	6.4	3.1	2.4	0.7
	80	25.6	533	4.3	533	4.3	12.2	109	7.3	3.0	2.1	0.6
	90	28.8	600	5.4	600	5.4	15.4	109	8.2	2.8	1.9	0.5
	100	32.0	667	6.7	667	6.7	19.0	109	9.1	2.4	1.7	0.5
	110	35.2	733	8.1	733	8.1	23.0	109	10.0	1.9	1.5	0.4
	120	38.4	800	9.6	800	9.6	27.4	109	10.9	1.3	1.4	0.4

					conversion factor / 𝑄̇out / [MW] (thermal output) / E*out , Pel,in, / [MW]

## Plots
Data rearranged for plotting

Site	case	Political region	Geological region	Rock layer	Reservoir	zres	east	north	Latitude	Longitude	Pth,out	Pel,brutto	ηel	Pth,in	WHTprod	WHTinj	WHPprod	cp	ρ	Production rate V̇	Production rate V̇	Production rate V̇	ṁ	Pth,well,cp					pESP,in	pESP,out	PESP,hyd	PESP,rot			PESP,el	Pcirc,el	Pprod,el	#BEZUG!	ηprod,tot	ηVSD	pinj,in	pinj,out	Pinj,hyd	Pinj,rot	Pinj,rot	ηinj,tot	Pinj,el	Pel,in,brineLoop	Pel,ORC	Pel,aux	Pel,netto	ε	Error +	Error-	#BEZUG!	T_m	Quality	Exergy flow				ζFlow	ζFlow	Error +	Error-	ζCarnot	ΔT
					MWth	MWel		MWth	°C	°C		J/kg/K	kg/m³	m³/h		l/s	kg/s	MWth					bar	bar	MWmech	MWmech			MWel		MWel	#BEZUG!			bar	bar	MWmech	MWmech			MWel					#BEZUG!					0 °C	20 °C				°C
Klaipeda			Baltic Basin					#DIV/0!				39°	11°		3844	1054		337.5	150	98.76437763	17					0.049	#BEZUG!					0.492					31					0.31					2.6	0.50			0.8	28
Neustadt-Glewe (GeotIS)		NE Germany	North-German Basin					8.8	3.32537734	0.13186	25.219	114°	57.888673				523.8		143		34.0					34	80	0.6693					1.308	#BEZUG!	0.511697248		8.9	13.86	0.072168				0.14187					23					-					-	-			-	56
Mezőberény		Lithuania	Pannonian Basin					80°	50		4177	975			11		1					0					0.021	#BEZUG!					0.011	0.031990985				41	7.2	4.9					7.9	5.4	1.4	0.9		30
Dürrnhaar		Bavaria	South-German Basin					6			138°	50		4214	928	486		135	125.3150789	46.5					1.350	#BEZUG!					0.000					34					0.25					9.2	7.1			0.8	88
Freiham		Bavaria	South-German Basin					13				89°	60		4190	966	396		110	106.3037875	12.9					0.735	#BEZUG!					0.000					18					0.21					3.8	2.7			0.9	29
Riem		Bavaria	South-German Basin					13				95°	55		4191	962	306		85	81.79636193	13.7					0.500	#BEZUG!					0.000					27					0.21					5.9	4.3			0.8	40
Neustadt-Glewe		NE Germany	North-German Basin					2.6	0.23	0.088461538		97°	71.3		3360.922094	1122	103.7		29	32.31800696	4.0					0.163	#BEZUG!					16					0.23					3.9	2.9			0.9	26
Kirchstockach		Bavaria	South-German Basin					6			130°	40		4205	935	486		135	126.2534534	47.8					1.000	#BEZUG!					0.000					48					0.24					11.1	8.5			0.8	90
Traunreut		Bavaria	South-German Basin					114°	57.2		4201	948			146	137.9737625	32.7					1.308	#BEZUG!					0.142					23					0.24					5.6	4.3			0.8	56
Unterhaching		Bavaria	South-German Basin					123°	59.3		4206	941	540		140		35.5					1.650	#BEZUG!					0.000					21					0.25					5.3	4.2			0.8	64
Bruchsal		Pfalz	Rhinegraben					0.55			126°	66.8				86.4		24	25	5.4					0.133	#BEZUG!					0.000					41					0.26					10.6	8.4			0.8	59
Sauerlach		Bavaria	South-German Basin					4	5			140°	38		4211	926	396		110	101.9126061	43.8					1.200	#BEZUG!					0.000					36					0.25					8.8	6.8			0.7	102
Laufzorn/Oberhaching		Bavaria	South-German Basin					40	4.3			127°	60				324		90		40.0					0.759	#BEZUG!					53					0.25					13.3	10.4			-	67
Traunreut		Bavaria	South-German Basin					99°	60		3287	1136	14.89		4	4.696802333	0.6					0.099	#BEZUG!					0.043					4					0.24					5.3	4.1			0.8	39
Groß Schönebeck real		NE Germany	North-German Basin					140°	60		3313	1111	14.89		4	4.595219444	1.2					0.099	#BEZUG!					0.043					9					0.22					1.0	0.7			0.8	80
Groß Schönebeck expected		NE Germany	North-German Basin					38	3.36	0.13186	25.48157136	123°					540		150		63.5					1.471	#BEZUG!					0			0.000					43					0.27					2.3	1.8			0.8	#WERT!
Unterhaching		Bavaria	South-German Basin					3.36			123°	59.28131794		4206	941			140	131.7143741	35.5					1.650	#BEZUG!					0			0.000					21					-					-	-			-	64
Laufzorn/Oberhaching		Bavaria	South-German Basin					40	4.3			128°	50		4209	935	504		140	130.9295072	40.0					1.300	#BEZUG!					0.000					31					0.24					7.5	5.8			0.8	78
Unterhaching		Bavaria	South-German Basin					3.5			125°					576		160		40.0					1.350	#BEZUG!					30					0.25					7.1	5.6			0.8	#WERT!
Kirchstockach		Bavaria	South-German Basin					6			130°	45		4207	935	486	486	135	126.2534534	45					357577.2571	45.14536356					1	#BEZUG!					0	1				45	2.6	2.6			0.23					10.8	8.3	0.4	0.4	0.7	85
Dürrnhaar		Bavaria	South-German Basin					6			138°	45		4212	928	486	486	135	125.3150789	49					391746.0328	49.09168501					1.35	#BEZUG!					0	1.35				36	1.9	1.9			0.24					9.0	7.0	0.3	0.3	0.7	93
Sauerlach		Bavaria	South-German Basin					4	5			140°	43		4213	926	396	396	110	101.9126061	42					408663.4399	41.64795618					1.2	#BEZUG!					0	1.2				35	1.8	1.8			0.24					8.5	6.6	0.2	0.2	0.7	97
		Pfalz	Rhinegraben					0.30					-	-			0.8	0
Soultz-sous-Forêts		Pfalz	Rhinegraben					1.7			150°	70		3907	983	109.8806609		31	30	9.4					1.000	39.153	0.116					0.166	#BEZUG!	0.700		1.000	39.153	0.114				0.000					56					-					16.0	13.1			-	80
Rittershoffen		Alsace/France	Rhinegraben					0.31					26.8	22.5			0.8	0
Landau		Pfalz	Rhinegraben					5	3			160°	50		3836.647568	982	252		70	68.72991816	29.0					0.600	#BEZUG!					0.000					48					0.27					13.2	10.6				110
Insheim		Pfalz	Rhinegraben					4.8			165°	70		3836.647568	982	288		80	78.54847789	28.6					0.800	#BEZUG!					0.000					36					0.30					10.6	8.8			0.8	95
Klaipeda		Lithuania	Baltic Basin					38°	16		3844	1053	201		56	58.81967379	5.0					17.25	45.96	0.1602975				0.1881488		0.276	#BEZUG!	0.580				0.153				0.221					10					0.09…0.09					0.9	0.2			0.73…0.73	22
Klaipeda		Lithuania	Baltic Basin					200…350					0.1602975					#BEZUG!					0.049					0.09					-			0.7	#WERT!
Klaipeda		Lithuania	Baltic Basin					-	0
Klaipeda		Lithuania	Baltic Basin					0.09					0.7	0
Klaipeda		Lithuania	Baltic Basin					0.09					0.7	0
Klaipeda		Lithuania	Baltic Basin					0.09					0.7	0
Klaipeda		Lithuania	Baltic Basin					210…280					#BEZUG!					0.09					-			0.7	#WERT!
Rittershoffen		Alsace/France	Rhinegraben					24	0			170°	80	25	3915	968	260.3003559	269.5967972	75	72.5	26	25.16336921	0.181859649					3.15					1	0.260	#BEZUG!	2.5					0	0.259799498				101	14.6	14.6			0.28					31.4	26.3	4.6	4.6	0.8	90
Mezőberény summer		Hungary	Pannonian Basin					80	50		4177	975	30		8	8.125	1.0					0.013	#BEZUG!					0.013					38					7.3				0.8…0.8
Mezőberény winter		Hungary	Pannonian Basin					80	50		4177	975	46		13	12.45833333	1.6					0.023	#BEZUG!					0.018					39					7.4				0.8
Mezőberény summer		Hungary	Pannonian Basin					80	50		4177	975	30		8	8.125	1.0					0.0055		0.013	#BEZUG!					0.008					48					9.2				0.8
Mezőberény winter		Hungary	Pannonian Basin					80	50		4177	975	46		13	12.45833333	1.6					0.011		0.023	#BEZUG!					0.012					45					8.6				0.8
Mezőberény summer		Hungary	Pannonian Basin					80	50		4177	975	30		8	8.125	1.018					0.000	6.971	0.006				0.008		0.020	#BEZUG!	0.700		7.500	11.719	0.004				0.005					40					7.7				0.8
Mezőberény winter		Hungary	Pannonian Basin					80	50		4177	975	46		13	12.45833333	1.561					0.000	10.688	0.014				0.020		0.032	#BEZUG!	0.700		8.500	14.970	0.008				0.012					36					6.9				0.8
#BEZUG!		Hungary	Pannonian Basin					#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!		#BEZUG!	#BEZUG!	#BEZUG!		#BEZUG!	#BEZUG!	#BEZUG!					#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!			#BEZUG!		#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!	#BEZUG!			#BEZUG!					#BEZUG!					#BEZUG!				0.8
Generic best case		#BEZUG!	#BEZUG!					150	45		4000	1000	184.32635		51.20176389	51.20176389	21.50474083					2	206.2981	#BEZUG!	#BEZUG!			#BEZUG!		1.494346154	#BEZUG!	0.7		10	175.5197	0.84749006				1.210700085					8					2.1				#BEZUG!
					Tinj vs. Tprod / production temperature Tprod / [°C] / reinjection temperature Tinj / [°C]
P vs. T / production temperature Tprod / [°C] / Pth / [MW]

𝜀 / energy conversion efficiency / 𝜀= Q̇out/Ẇel,in					ε vs. Pth / Pth/[MW] / energy conversion efficiency / 𝜀= Q̇out/Ẇel,in					𝜀 vs. T / production temperature Tprod / [°C] / energy conversion efficiency / 𝜀= Q̇out/Ẇel,in					ε vs. V̇ / Production rate V̇ / [l/s] / energy conversion efficiency / 𝜀= Q̇out/Ẇel,in

ζ / exergy conversion efficiency / ζ= Ė*out/Ẇel,in					ζ vs. Pth / Pth / [MW] / exergy conversion efficiency / ζ= Ė*out/Ẇel,in

					𝜀, ζ vs. ΔT / ΔT / [K] / energy conversion efficiency / 𝜀= Q̇out/Ẇel,in / exergy conversion efficiency / ζ= Ė*out/Ẇel,in
𝜀, ζ / 𝜀= Pth/Pel,in / 𝜀 exergy onversion efficiency					𝜀, ζ vs. T / production temperature Tprod / [°C] / energy conversion efficiency / 𝜀= Q̇out/Ẇel,in / exergy conversion efficiency / ζ= Ė*out/Ẇel,in with T0=0 °C

## Reference_efficiencies
Conversion efficiency of …

Tout	100	°C	temperature of heat provision
Tamb	0	°C	Ambient temperature
Tm	47.4	°C	Logarithmic mean temperature of heat transfer
… an electric heater
ε	1		energy conversion efficiency
ζ	0.27		exergy conversion efficiency

… an ideal heat pump:
εCarnot, COPideal	3.73		energy conversion efficiency
ζCarnot	100%		exergy conversion efficiency

## References
GAB2017	https://www.es.mw.tum.de/fileadmin/w00bhq/www/pdf/Potential_der_hydrothermalen_Geothermie_zur_Stromerzeugung_in_Deutschland.pdf
Bauer2014	https://books.google.de/books?id=Vd8oBAAAQBAJ&pg=PA737&lpg=PA737&dq=gr%C3%BCnwald+laufzorn+injektion+temperatur&source=bl&ots=5aFV3UFoi0&sig=-9LM__EHhEBZ05vD-cw09sBhMFM&hl=de&sa=X&ved=0ahUKEwjsrJXwrJfcAhVPbVAKHajUBMsQ6AEINjAB#v=onepage&q=gr%C3%BCnwald%20laufzorn%20injektion%20temperatur&f=false
Schlagermann2014	http://www.researchgate.net/publication/264905299_Exergokonomische_Analyse_geothermischer_Strombereitstellung_am_Beispiel_des_Oberrheingrabens

## 'file:///D:/francke/Eigene%20Dateien/GFZ/Publikationen/2021/Energy%20conversion%20efficiency%20of%20Geothermal%20plants/BrineProp_0.58_COP%20Geothermal.xlsm'#1phase_Liq_Neustadt-Glewe
1121.9365963816379
3360.9220936078987

## 'file:///D:/francke/Eigene%20Dateien/GFZ/Promotion/Material/Loggingdaten/2012-03%201%20Woche%20Dauerbetrieb/1204170800-1204241530-10minAvg-ALL.xlsb'#1204170800-1204241530-10minAvg-
43089.112130183443

## 'file:///D:/francke/Eigene%20Dateien/GFZ/Publikationen/2021/Energy%20conversion%20efficiency%20of%20Geothermal%20plants/Klaipeda/BrineProp_0.55_Klaipeda.xlsm'#1phase_Liquid
3843.5604418524968