Supplementary Information

Assessment of microplastics in a municipal wastewater treatment plant with tertiary treatment: Removal efficiencies and loading per day into the environment

Javier Bayo *, Sonia Olmos, Joaquín López-Castellanos

Department of Chemical and Environmental Engineering, Technical University of Cartagena, Paseo Alfonso XIII 44, E-30203 Cartagena, Spain

* Corresponding author: javier.bayo@upct.es (J. Bayo)

Table S1. Description of sewage treatment stages and working parameters.

| DESIGNED FLOWS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Daily average flow |  | Hourly average flow | Peak hourly flow | Maximum hourly flow |
| 6,500 m3 d-1 |  | 271 m3 h-1 | 677 m3 h-1 | 1,354 m3 h-1 |
| CONVENTIONAL TREATMENT LINE (ACTIVATED SLUDGE PROCESS) |  |  |  |  |
| Coarse solids | Concrete casting box for coarse solids removal with a volume of 22.79 m3. Extraction by means of a 250 L amphibious clamshell grab moved by 1,000 kg electric hoist. |  |  |  |
| Pretreatment | Initial screening with a 50 mm mesh for rough solids, 3 automatic screens with a 12 mm pitch and 3 self-cleaning sieves (3 mm clearance for fine solids). |  |  |  |
| Grit and grease | Aeration using 2+1 double speed blowers of 213/105 m3 h and 4.90/3.20 kW. |  |  |  |
| Phosphorus removal | Biological removal of phosphorus through anaerobic chambers of 1,160 m3, divided into 4 chambers per line and one shaker per chamber to promote agitation and avoid sedimentation. |  |  |  |
| Biological reactor | Two full-scale Carrousel oxidation ditch systems with prolonged aeration (8,502 m3 each), 182 membrane diffusers, and three 4.0 kW current accelerators per line. They are equipped with an internal pre-anoxic zone for nitrogen removal. |  |  |  |
| Secondary clarifiers and sludge treatment | Two circular gravity clarifiers (21 m inner Ø). Settled sludge is collected and partially pumped to the biological reactor by means of 2+1 submersible centrifugal pumps. Secondary sludge in excess is thickened by a gravity thickener (12 m inner Ø) and dewatered by means of 2 centrifuges (10 m3/h) with prior addition of polyelectrolyte. |  |  |  |
| Tertiary treatment and UV disinfection | Three parallel rapid sand filters with high purity siliceous sand (85% minimum content of silica, 20.5 tons/filter) and two units per filter, with a total surface of 62.18 m2. Other parameters: - Effective grain size (mm) 1.2 ± 0.05 - Sand bulk density (g ml-1) 2.5 - Uniformity coefficient (d10/d60) 1.5 Ultraviolet disinfection performance in an open-channel with a maximum operating power of 34.60 kW. |  |  |  |

Table S2. Physicochemical and biological parameters.

| RAW WASTEWATER |  |
| --- | --- |
| Parameter | Concentration (daily load) |
| BOD5 | 650 mg l-1 (4,225 kg d-1) |
| TSS | 500 mg l-1 (3,250 kg d-1) |
| TN | 60 mg l-1 (390 kg d-1) |
| TP | 15 mg l-1 (98 kg d-1) |
| EFFLUENT |  |
| Parameter | Concentration |
| BOD5 | ≤ 25 mg l-1 |
| TSS | ≤ 35 mg l-1 |
| TN | ≤ 15 mg l-1 |
| TP | ≤ 2 mg l-1 |
| TC | 2.2 cfu 100 ml-1 |
| T | 2 NTU |
| NE | 1 egg l-1 |

BOD5: Biochemical oxygen demand-5 days; TSS: Total suspended solids; TP: Total phosphorus; TN: Total nitrogen; TC: Total coliforms (colony-forming units); T: Turbidity (nephelometric turbidity units); NE: Nematode eggs.

Table S3. Samples and volumes collected in “La Aljorra” WWTP for this study.

| DATE | VOLUME (L) |  |  |
| --- | --- | --- | --- |
|  | INF | EFF | TOTAL |
| Feb 28th, 2019 | 4.500 | 7.320 | 11.82 |
| Mar 20th, 2019 | 4.725 | 4.830 | 9.555 |
| Apr 25th, 2019 | 3.610 | 3.000 | 6.610 |
| May 30th, 2019 | 4.500 | 4.480 | 8.980 |
| Jul 3rd, 2019 | 4.500 | 4.810 | 9.310 |
| Aug 1st, 2019 | 2.400 | 7.740 | 10.140 |
| Sep 19th, 2019 | 4.650 | 8.890 | 13.540 |
| Oct 17th, 2019 | 3.820 | 5.210 | 9.030 |
| Nov 21st, 2019 | 3.650 | 6.820 | 10.470 |
| Dec 19th, 2019 | 3.450 | 6.780 | 10.230 |
| Jan 23rd, 2020 | 4.850 | 7.270 | 12.120 |
| Feb 20th, 2020 | 6.230 | 7.500 | 13.730 |
| Mar 12th, 2020 | 4.500 | 5.720 | 10.220 |
| May 20th, 2020 | 4.500 | 6.470 | 10.970 |
| JAN 22/2018 | 3.320 | 3.500 | 3.460 |
| FEB 08/2018 | 2.950 | 3.050 | 1.375 |
| FEB 22/2018 | 3.270 | 3.250 | 3.220 |
| MAR 15/2018 | 3.100 | 3.190 | 3.000 |
| APR 18/2018 | 3.220 | 3.300 | 3.120 |
| TOTAL | 59.885 | 86.840 | 146.725 |

Fig. S1. Location of “La Aljorra” WWTP (37º41’16’’N, 01º03’13’’W).

Fig. S2. Unidentified fibers from “la Aljorra” WWTP: (a-e) INF and (f-j) EFF.