| NOMENCLATURE |  |  |  |
| --- | --- | --- | --- |
| L | Total length of microchannels(mm) | h | Surface heat transfer coefficient( W/(㎡·K) |
| W | Total length of microchannels in the computational domain(mm) | Q | the total heat input at the heating bottom(W) |
| H | Total height of microchannels(mm) | q | the heat flux input at the bottom of the heating(W/m2) |
| ρ | Density(kg/m3) | Nu | Nusselt number |
| u | Velocity(m/s) | Sgen | entropy generation(W/K) |
| p | Pressure(Pa) | P | Pump power(W) |
| T | Temperature(K) | m | mass flow(kg/s) |
| c | the specific heat capacity(J/(kg·K)) | Rth | Thermal resistance(K/W) |
| k | thermal conductivity(W/(m∙K)) | PEC | Performance Evaluation Criteria |
| t | Temperature(℃) | Subscripts |  |
| Re | The Reynolds number | f | fluid |
| μ | dynamic viscosity(N·s/m2) | s | solid |
| Dh | equivalent diameter(m) | in | inlet |
| A | Cross sectional area of microchannels(mm2) | con | the convective heat exchange surface |
| χ | Cross-sectional perimeter of microchannels(m) | h | the heating surface |
| f | Friction resistance coefficient |  |  |

Table 1. Microchannel geometry parameters.

| Geometry | MC-DLRC | MC-DLCFRC | MC-DLTC | MC-DLCC | MC-DLHRC |
| --- | --- | --- | --- | --- | --- |
| Geometric parameters | WN、HN | WC、HC | WT1、WT2、HT | WR | WS |
| Values（mm） | 1, 0.6 | 1, 0.6 | 1.92, 0.64, 0.64 | 0.75 | 1.22 |
| Hydraulic radius,（mm） | 0.1875 | 0.1875 | 0.1875 | 0.1875 | 0.1875 |

Table 2. Boundary conditions

| Zone | Boundary condition | Expression |
| --- | --- | --- |
| Inlet (x=0) | Velocity-inlet | u=uf=( 0.135, 0.269, 0.404, 0.539, 0.673, 0.808,0.943,1.077, 1.212, 1.347 ) Tf=Tin=293K, kf=∂Tf∂x0(fluid),kf=∂Ts∂x=0(solid) |
| Outlet (x=60mm) | Pressure-outlet | pf=pout=0(gauge pressure), |
| Bottom wall (y=0) | Constant heat flux | kf=∂Tf∂Z=q=106W/m2 |
| z=0 and z=6mm | Symmetry | ∂Ts∂Z=0 |
| Upper wall (y=2mm) | Adiabatic | -ks∂Ts∂y=0, -kf∂Tf∂y=0 |
| Inner walls for fluid/solid surface | No-Slip, NO-Penetration | -ks∂Ts∂n=-kf∂Tf∂y(where n is the coordinate normal to the wall) |

Table 3. Relative error of grid testing

| Total number of grids |  | ∆p（Pa） | e（%） | Nu | e（%） |
| --- | --- | --- | --- | --- | --- |
| MC-DLRC | 428270 | 1519.013 | 14.08 | 98.833 | 7.09 |
|  | 1100018 | 1668.372 | 5.66 | 102.731 | 3.43 |
|  | 2703932 | 1748.639 | 1.13 | 105.251 | 1.05 |
|  | 3670109 | 1768.937 | 0 | 106.378 | 0 |