Fig.S1. Overview of eight sub-regions related to WDN case study

| (a) | (b) |
| --- | --- |

## Fig.S2. Overview of apparatuses, (a) handy GPS used in this study and (b) installation of handy GPS software on the cellphone

- Recorded in 2014/08/14

(b) Recorded in 2014/10/08

(c) Recorded in 2014/04/30

(d) Recorded in 2014/07/02

(e) Recorded in 2014/08/16

(f) Recorded in 2014/04/30

(g) Recorded in 2014/10/07

Fig.S3. Various pipe breaks observed in the Azadshahr sub-region of WDN for various reasons, (a) excavation operation, (b) rusty water pipe, (c) leak, (d) pressure fluctuation, (e) settlement, (f) heavy vehicles, and (g) inappropriate operation

Fig.S4. Variations of DDR values against data samples for MARS model

Fig.S5. Variations of DDR values against data samples for GEP model

Fig.S6. Variations of DDR values against data samples for M5 technique

Table S1. Characterizations of the first region of Yazd’s WDN

| Eight sub-regions of WDN case study |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Zone Identification | Z1 | Z2 | Z3 | Z4 | Z5 | Z6 | Z7 | Z8 |
| Number of Incepted Pipes | 99 | 45 | 26 | 77 | 57 | 335 | 36 | 176 |
| Length of Incepted Pipes (km) | 10.1 | 4.264 | 6.052 | 9.53 | 9.94 | 56.32 | 6.064 | 29.329 |
| Pipe Age (yr) | 2-7 | 1-8 | 1-8 | 1-8 | 3-10 | 2-7 | 1,2,3,5 | 1,2,3,5,6 |
| Nominal Pipe Diameter (mm) | 63-150 | 63-150 | 63-150 | 63-150 | 63-150 | 63-150 | 63-150 | 63-150 |
| Depth pf Pipe Installation (m) | 1 | 1 | 1 | 1.1 | 1.2 | 1 | 1.1 | 1 |
| Pressure (bar) | 1.5 | 2 | 1.8 | 1.8 | 2 | 2 | 1.7 | 2 |
| Number of Failure | 123 | 90 | 29 | 89 | 44 | 408 | 44 | 206 |
| Break Rate of Pipe | 0.46-77.7 | 0.37-21.49 | 0.03-25.31 | 0.22-20.33 | 0.024-11.90 | 0.27-2.51 | 0.49-4.21 | 0.408-4.165 |

Table S1. List of 17 if-then rules applied for pipes break rate

if LP <= 0.0235 BRP=33.174-3.913×AP else if LP<= 0.092 if AP<= 4.5 if AP<= 1.5 BRP=17.460-132.679×LP else BRP=15.895-77.999×LP-1.104×AP-2.299×PA else if LP<= 0.048 if LP<= 0.040 BRP=11.792-94.289×LP-0.464×AP-1.647×PA else BRP=2.432 else BRP=4.165-23.158×LP-0.174× AP else if AP<= 2.5 if P<=1.9 BRP=4.420-0.966×AP else BRP=1.703 else

Table S1. (Continued)

if LP<= 0.113 if AP<= 4.5 BRP=1.979 else BRP=2.301-0.191×AP else if AP<= 3.5 if LP<= 0.148 BRP=1.544 else if LP<= 0.187 if LP<= 0.164 BRP=1.243 else BRP=0.983 else BRP=2.600-4.761×LP else if AP<=5.5 if LP<=0.128 BRP=0.928 else BRP=1.934-0.087×AP-0.386×PA Else BRP=1.903-0.664×PA

Table S3. List of BFs used in the MARS model

| Coefficients (β) | Basis Function |
| --- | --- |
| 78.792 | BF1 = max(0, 0.06476 –LP)×max(0, 2-AP) |
| -0.302 | BF2 = max(0, AP-3) |
| 1.768 | BF3 = max(0, 3-AP) |
| -4.253 | BF4 = max(0, 3-AP)×max(0, LP-0.032036) |
| 116.099 | BF5 = max(0, 3-AP)×max(0, 0.032036-LP) |
| 19.423 | BF6 = max(0, LP-0.1375) |
| 393.595 | BF7 = max(0, 0.02148-LP) |
| -1717.432 | BF8 = max(0, 0.02148-LP)×max(0, 1.2-hP) |
| 2.408 | BF9 = max(0, PA-1.7) |
| 101.444 | BF10 = max(0, 1.7- PA) |
| -10598.771 | BF11 = max(0, 1.7- PA)×max(0, LP-0.02148) |
| 4659.487 | BF12 = max(0, 1.7- PA)×max(0, 0.02148-LP) |
| 8.400 | BF13 = max(0, 0.1375-LP)×max(0,AP-5) |
| 0.612 | BF14 = max(0, PA-1.7)×max(0, AP-2) |
| -18.453 | BF15 = max(0, LP-0.04362) |
| 108.287 | BF16 = max(0, 0.04362-LP)×max(0, 4-AP) |
| 21.935 | BF17 = max(0, 0.1375-LP)×max(0, 2-AP) |
| -14835.222 | BF18 = max(0, 1.7-PA)×max(0, 0.02886-LP) |
| 206.372 | BF19 = max(0, 0.03051-LP) |
| -73.898 | BF20 = max(0, LP-0.03051)×max(0, PA-1.7) |
| 10579.230 | BF21 = max(0, LP-0.03051)×max(0, 1.7- PA) |
| 147.098 | BF22 = max(0, 0.06476 -L)×max(0, 2- PA) |
| 68.513 | BF23 = max(0, PA-1.7)×max(0, LP-0.08654) |
| 5331.760 | BF24 = max(0, 1.7- PA)×max(0, 0.02435-LP) |
| -9.547 | BF25 = max(0, 0.1375-LP)×max(0,AP-4) |
| -31.254 | BF26 = max(0, 0.1375-LP)×max(0, 1.8- PA) |

Table S4. Control parameters used in the GEP model

| Parameter | Description of parameter | Setting of parameter |
| --- | --- | --- |
| P1 | Function set | times, minus, plus, square, tanh, exp |
| P2 | Population size | 200 |
| P3 | Mutation frequency | 0.94 |
| P4 | Crossover frequency (%) | 50 |
| P5 | Number of replication | 10 |
| P6 | Block mutation rate (%) | 30 |
| P7 | Instruction mutation rate (%) | 30 |
| P8 | Instruction data mutation rate (%) | 40 |
| P9 | Maximum depth of tree | 7 |
| P10 | Program size | Initial 64, Maximum 256 |
| P11 | Number of gene | 3 |

Table S5. Results of statistical distributions

| Variables | Distribution Type | Mean | Coefficient of Variation |
| --- | --- | --- | --- |
| LP(km) | Lognormal | 0.155 | 1.6990 |
| hP(m) | Normal | 1.030 | 0.0569 |
| AP(yr) | Normal | 4.684 | 0.3426 |
| PA(bar) | Lognormal | 1.877 | 0.0975 |
| BRP | Lognormal | 1.753 | 1.3243 |