[bookmark: _Hlk137657143]APPENDIX 1
REBOUND HAMMER TEST RESULTS







	Block A    Last floor beam-spall
Angle = +90 Degree
	
	Block A   Last floor s30lab (Toilet)--damp
Angle = +90 Degree

	S/N
	Rebound value
	Compressive strength value (MPa)
	
	S/N
	Rebound value
	Compressive strength value (MPa)

	1
	28
	14.00
	
	1
	40
	32.00

	2
	25
	10.00
	
	2
	40
	32.00

	3
	30
	16.00
	
	3
	38
	29.00

	4
	29
	15.00
	
	4
	39
	30.00

	5
	28
	14.00
	
	5
	40
	32.00

	6
	25
	10.00
	
	6
	38
	29.00

	7
	30
	16.00
	
	7
	37
	27.00

	8
	30
	16.00
	
	8
	39
	30.00

	9
	26
	11.00
	
	9
	41
	34.00

	10
	27
	12.00
	
	10
	40
	32.00

	24
	AVERAGE
	13.40
	
	32
	AVERAGE
	30.70




	Block A First-floor Stair wall--damp algae
Angle = 0 Degree
	
	Block A First-floor Slab (Toilet )--damp
Angle = +90 Degree

	S/N
	Rebound value
	Compressive strength value (MPa)
	
	S/N
	Rebound value
	Compressive strength value (MPa)

	1
	20
	10.00
	
	1
	40
	32.00

	2
	25
	16.00
	
	2
	39
	30.00

	3
	23
	13.50
	
	3
	37
	27.00

	4
	29
	22.00
	
	4
	40
	32.00

	5
	28
	20.00
	
	5
	40
	32.00

	6
	25
	16.00
	
	6
	38
	29.00

	7
	26
	17.00
	
	7
	37
	27.00

	8
	30
	23.00
	
	8
	38
	29.00

	9
	26
	17.00
	
	9
	40
	32.00

	10
	27
	18.00
	
	10
	41
	34.00

	30
	AVERAGE
	17.25
	
	32
	AVERAGE
	30.40





	Block A    Ground floor column-mild damp
Angle = 0 Degree

	S/N
	Rebound Value
	Compressive strength Value (MPa)

	1
	30
	23.00

	2
	29
	22.00

	3
	30
	23.00

	4
	29
	22.00

	5
	30
	23.00

	6
	30
	23.00

	7
	30
	23.00

	8
	30
	23.00

	9
	29
	22.00

	10
	27
	18.00

	26
	AVERAGE
	22.20





	Block B Second-floor column-damp mould
Angle = 0 Degree
	
	Block B Second-floor Slab (Toilet)-damp
Angle = +90 Degree

	S/N
	Rebound value
	Compressive strength value (MPa)
	
	S/N
	Rebound value
	Compressive strength value (MPa)

	1
	32
	26.00
	
	1
	39
	30.00

	2
	32
	26.00
	
	2
	40
	32.00

	3
	32
	26.50
	
	3
	37
	27.00

	4
	34
	29.70
	
	4
	37
	27.00

	5
	34
	29.70
	
	5
	40
	32.00

	6
	32
	26.00
	
	6
	38
	29.00

	7
	30
	23.00
	
	7
	40
	32.00

	8
	33
	28.00
	
	8
	35
	24.00

	9
	30
	23.00
	
	9
	40
	32.00

	10
	32
	26.00
	
	10
	41
	34.00

	27
	AVERAGE
	26.39
	
	32
	AVERAGE
	29.90

	Block B    First-floor Column-damp mould
Angle = 0 Degree
	
	Block B First-floor Slab (Toilet)-seru seep
Angle = +90 Degree

	S/N
	Rebound value
	Compressive strength value (MPa)
	
	S/N
	Rebound value
	Compressive strength value (MPa)

	1
	32
	26.00
	
	1
	37
	27.00

	2
	34
	29.70
	
	2
	37
	27.00

	3
	32
	26.00
	
	3
	38
	29.00

	4
	32
	26.00
	
	4
	38
	29.00

	5
	34
	29.70
	
	5
	28
	14.00

	6
	32
	26.00
	
	6
	35
	24.00

	7
	30
	23.00
	
	7
	35
	24.00

	8
	32
	26.00
	
	8
	28
	14.00

	9
	30
	23.00
	
	9
	37
	27.00

	10
	30
	23.00
	
	10
	30
	16.00

	27
	AVERAGE
	25.84
	
	34
	AVERAGE
	23.10





	Block C   Ground floor column-damp mould
Angle = 0 Degree
	
	Block C   Ground floor beam--spall
Angle = +90 Degree

	S/N
	Rebound value
	Compressive strength value (MPa)
	
	S/N
	Rebound value
	Compressive strength value (MPa)

	1
	32
	26.00
	
	1
	28
	14.00

	2
	34
	29.70
	
	2
	28
	14.00

	3
	30
	23.00
	
	3
	34
	22.00

	4
	30
	23.00
	
	4
	32
	20.00

	5
	34
	29.70
	
	5
	32
	20.00

	6
	32
	26.00
	
	6
	30
	16.00

	7
	30
	23.00
	
	7
	30
	16.00

	8
	31
	24.00
	
	8
	28
	14.00

	9
	29
	22.00
	
	9
	28
	14.00

	10
	29
	22.00
	
	10
	30
	16.00

	27
	AVERAGE
	24.84
	
	30
	AVERAGE
	16.60




	Block C   Second-floor Slab (Toilet) damp
Angle = +90 Degree

	S/N
	Rebound Value
	Compressive strength Value (MPa)

	1
	40
	32

	2
	39
	30

	3
	37
	27

	4
	40
	32

	5
	45
	42

	6
	38
	29

	7
	37
	27

	8
	41
	34

	9
	40
	32

	10
	35
	24

	32
	AVERAGE
	30.90





	Block D Ground Floor Slab-damp seep crk
Angle = +90 Degree
	
	Block D Ground Floor Column -damp
Angle = 0 Degree

	S/N
	Rebound Value
	Compressive strength Value (MPa)
	
	S/N
	Rebound Value
	Compressive strength Value (MPa)

	1
	35
	24.00
	
	1
	37
	34.00

	2
	37
	27.00
	
	2
	38
	36.00

	3
	38
	29.00
	
	3
	33
	28.00

	4
	39
	31.00
	
	4
	39
	38.00

	5
	32
	20.00
	
	5
	35
	31.00

	6
	35
	24.00
	
	6
	35
	31.00

	7
	37
	27.00
	
	7
	37
	34.00

	8
	35
	24.00
	
	8
	39
	38.00

	9
	35
	24.00
	
	9
	36
	33.00

	10
	32
	20.00
	
	10
	33
	28.00

	33
	AVERAGE
	25.00
	
	35
	AVERAGE
	33.1




	Block D First floor Slab(Toilet )-spalling
Angle = +90 Degree
	
	Block D Second floor slab- crack
Angle = +90 Degree

	S/N
	Rebound value
	Compressive strength value (MPa)
	
	S/N
	Rebound value
	Compressive strength value (MPa)

	1
	35
	24.00
	
	1
	34
	22.00

	2
	34
	22.00
	
	2
	32
	20.00

	3
	38
	29.00
	
	3
	35
	24.00

	4
	37
	27.00
	
	4
	39
	30.00

	5
	32
	20.00
	
	5
	40
	32.00

	6
	32
	20.00
	
	6
	33
	21.00

	7
	33
	21.00
	
	7
	31
	18.00

	8
	34
	22.00
	
	8
	39
	30.00

	9
	34
	22.00
	
	9
	35
	24.00

	10
	32
	20.00
	
	10
	34
	22.00

	32
	AVERAGE
	22.70
	
	32
	AVERAGE
	24.30





	Block E Ground floor column-damp
Angle = 0 Degree
	
	Block E First floor slab(toilet)-damp crack
Angle = +90 Degree

	S/N
	Rebound value
	Compressive strength value (MPa)
	
	S/N
	Rebound value
	Compressive strength value (MPa)

	1
	30
	23.00
	
	1
	38
	29.00

	2
	28
	20.00
	
	2
	32
	20.00

	3
	27
	18.00
	
	3
	34
	22.00

	4
	32
	26.00
	
	4
	38
	29.00

	5
	28
	20.00
	
	5
	37
	27.00

	6
	27
	18.00
	
	6
	33
	21.00

	7
	30
	23.00
	
	7
	36
	26.00

	8
	30
	23.00
	
	8
	35
	24.00

	9
	30
	23.00
	
	9
	35
	24.00

	10
	32
	26.00
	
	10
	34
	22.00

	26
	AVERAGE
	22.00
	
	30
	AVERAGE
	24.40




	Block E Second floor Slab(Toilet)-damp
Angle = 0 Degree
	
	Block E Second floor Slab-spall
Angle = +90 Degree

	S/N
	Rebound value
	Compressive strength value (MPa)
	
	S/N
	Rebound value
	Compressive strength value (MPa)

	1
	37
	27.00
	
	1
	30
	16.00

	2
	38
	29.00
	
	2
	30
	16.00

	3
	36
	26.00
	
	3
	32
	20.00

	4
	40
	32.00
	
	4
	38
	29.00

	5
	38
	29.00
	
	5
	37
	27.00

	6
	40
	32.00
	
	6
	33
	21.00

	7
	36
	26.00
	
	7
	36
	26.00

	8
	38
	29.00
	
	8
	30
	16.00

	9
	36
	26.00
	
	9
	30
	16.00

	10
	38
	29.00
	
	10
	34
	22.00

	30
	AVERAGE
	28.50
	
	30
	AVERAGE
	20.30



