## Sheet1
| Treatment Target | rBOD | [5 empty] | NIT |  |  | BNR
| Configuration (WERF code) | B1 | B2 | B3 | C1 | C2 | C3 | E2 | E2P | F1 | G1 | G2 | G3 | H1 | I1 | I2 | I3 | N1 | N2
Influent | Flow rate [MGD] | 10
| Coagulant dosage [gAl/m3] | NA | [11 empty] | 6.6 | NA
Primary Clarifier | Underflow rate [MGD] | 0.066 |  |  | NA |  |  | NA | 0.074 | 0.074 | 0.074 |  |  | 0.074 | NA |  |  | 0.074 | NA
| Solids removal efficiency [-] | 0.6 | [6 empty] | 0.6 | 0.6 | 0.6 |  |  | 0.6 |  |  |  | 0.6
Primary Sludge Thickening | Thickened sludge flowrate [MGD] | 0.023 | [6 empty] | 0.023 | 0.026 | 0.026 |  |  | 0.026 |  |  |  | NA
| Solids removal efficiency [-] | 0.9 | [6 empty] | 0.9 | 0.9 | 0.9 |  |  | 0.9
Activated Sludge Reactors | Zone 1 volume [MG] | 0.16667 |  |  | 0.26667 |  |  | 0.8 | 0.4 | 0.4 | 0.0658 |  |  | 0.4209 | 0.63 | 0.63 | 0.33 | 0.3132
| Zone 2 volume [MG] | 0.16667 |  |  | 0.26667 |  |  | 0.8 | 0.4 | 0.4 | 0.611 |  |  | 0.4209 | 1.5 | 1.5 | 1.5 | 0.4698
| Zone 3 volume [MG] | 0.16667 |  |  | 0.26667 |  |  | 0.8 | 0.4 | 0.4 | 0.6956 |  |  | 1.1492 | 2 | 2 | 2.1 | 0.6264
| Zone 4 volume [MG] | 0.16667 |  |  | 0.26667 |  |  | 0.8 | 0.4 | 0.4 | 0.6956 |  |  | 1.1492 | 2 | 2 | 2.1 | 0.6264
| Zone 5 volume [MG] | 0.16667 |  |  | 0.26667 |  |  | 0.8 | 0.4 | 0.4 | 1.316 |  |  | 0.4209 | 2.3 | 2.3 | 2.3 | 0.4698
| Zone 6 volume [MG] | 0.16667 |  |  | 0.26667 |  |  | 0.8 | 0.4 | 0.4 | 1.316 |  |  | 0.09882 | 0.21 | 0.21 | 0.31 | 0.1044
| Zone 1 DO setpoint [mg/L] | 2 | [8 empty] | 0 |  |  | 0 | 0 |  |  | 0
| Zone 2 DO setpoint [mg/L] | 2 | [8 empty] | 0 |  |  | 0 | 0 |  |  | 0
| Zone 3 DO setpoint [mg/L] | 2 | [8 empty] | 0 |  |  | 2 | 2 |  |  | 3
| Zone 4 DO setpoint [mg/L] | 2 | [8 empty] | 0 |  |  | 2 | 2 |  |  | 3
| Zone 5 DO setpoint [mg/L] | 2 | [8 empty] | 2 |  |  | 0 | 0 |  |  | 0
| Zone 6 DO setpoint [mg/L] | 2 | [8 empty] | 2 |  |  | 2 | 2 |  |  | 2
| Primary effluent (or raw influent + reject water) | 100% to zone 1 | [8 empty] | 80% to zone 2, 20% to zone 3 |  |  | 100% to zone 1 | 100% to zone 1 |  |  | 100% to zone 1
| RAS | 100% to zone 1 | [8 empty] | 100% to zone 1 |  |  | 100% to zone 1 | 100% to zone 1 |  |  | NA
| Internal recirculation #1 | NA | [8 empty] | 40 MGD from zone 6 to zone 3 |  |  | 30 MGD from zone 4 to zone 1 | 30 MGD from zone 4 to zone 2 |  |  | 10 MGD from zone 2 to zone 1
| Internal recirculation #2 | NA | [8 empty] | NA |  |  | NA | NA |  |  | 40 MGD from zome 4 to zone 2 | 20 MGD from zome 4 to zone 2
| Internal recirculation #3 | NA | [8 empty] | NA |  |  | NA | NA |  |  | 40 MGD from zone 6 to zone 3
| External carbon | NA | [8 empty] | 100% to zone 1 |  |  | 100% to zone 1 | NA |  |  | 100% to zone 1
| Carbon dosage [kgCOD/hr] | NA | [8 empty] | 85 | 85 | 30 | 43 | NA |  |  | 250 | 200
Membrane Unit | Zone 6 sludge wasting [MGD] | NA | [15 empty] | 0.17 | 0.3
| Solids capture rate [-] | [16 empty] | 0.9999
| Cleaning air flowrate [cfm] | [16 empty] | 20000
Final Clarifier | Surface area [sqft] | 17000 | [15 empty] | NA
| Height [ft] | 12
| Feed point from bottom [ft] | 7 |  |  | 5 |  |  | 5 | 5 | 7 | 7 |  |  | 7 | 5
| RAS flowrate [MGD] | 6.7 |  |  | 6.7 |  |  | 6.7 | 6.7 | 6.7 | 4 |  |  | 4 | 6.7
| WAS flowrate [MGD] | 0.2 |  |  | 0.32 |  |  | 0.33 | 0.163 | 0.163 | 0.135 | 0.136 | 0.14 | 0.1 | 0.2815
| Hindered zone settling parameter [m3/g TSS] | 0.0004 |  |  | 0.0003 |  |  | 0.0003 | 0.0003 | 0.0004 | 0.0004 |  |  | 0.0004 | 0.0003
| Flocculant zone settling parameter [m3/g TSS] | 0.0025 |  |  | 0.0052 |  |  | 0.0052 | 0.0052 | 0.1 | 0.1 |  |  | 0.1 | 0.0052
| Non-settleable fraction of TSS [-] | 0.001 |  |  | 0.001 |  |  | 0.001 | 0.001 | 0.01 | 0.01 |  |  | 0.01 | 0.001
| Maximum nonsettleable solids [mgTSS/L] | 20 | [5 empty] | 8 | [6 empty] | 20
WAS Thickening | Thickened sludge solids [%TS] | 5 | [15 empty] | NA | 5
| Solids removal efficiency [-] | 0.95 | [16 empty] | 0.95
Co-Thickening | Thickened sludge solids [%TS] | NA | [15 empty] | 5 | NA
| Solids removal efficiency [-] | [16 empty] | 0.85
Anaerobic Digestion | Liquid phase volume [MG] | 0.85 | NA | NA | 0.85 | NA | NA | NA | NA | 0.85 | 0.95 | NA | NA | 1.1 | 0.85 | NA | NA | 1.2 | NA
| Headspace volume [MG] | 0.085 |  |  | 0.085 |  |  |  |  | 0.085 | 0.117 |  |  | 0.11 | 0.085 |  |  | 0.12
| Biogas kLa [/d] | 10 |  |  | 10 |  |  |  |  | 10 | 10 |  |  | 10 | 10 |  |  | 10
Aerobic Digestion | Digester volume [MG] | NA | 3 | NA | NA | 3 | NA | 3 | 0.5 | NA | NA | 2.4 | NA | NA | NA | 2.4 | NA | NA | 2.4
| DO setpoint [mg/L] |  | 1 |  |  | 1 |  | 1 | 1 |  |  | 1 |  |  |  | 1 |  |  | 1
Sludge Dewatering | Cake solids [%TS] | 18 | 17 | 20 | 17 |  |  | 17 | 17 | 18 | 18 | 17 | 20 | 18 | 17 |  |  | 18 | 17
| Solids removal efficiency [-] | 0.9