Table 1  Characteristics of Film Fill Media for Heat Transfer

( Manufacturer: Film fill media for heat transfer, Icea, Fluid Handling, Casalbuttano, Italy )

| Product Code | CTPAK (Onda) 12, sheet spacing 12 mm | CTPAK (Onda) 19, sheet spacing 19 mm | CTPAK (Onda) 27, sheet spacing 27 mm |
| --- | --- | --- | --- |
| Property Description |  |  |  |
| (1) Operating temperature | Standard: -5 → +60 ºC | Standard: -5 → +60 ºC | Standard: -5 → +60 ºC |
| (2) Size : Length x Width x Depth | 900 → 2750 mm x up to 600 mm x up to 600 mm | 900 → 2750 mm x up to 600 mm x up to 600 mm | 900 → 2400 mm x up to 600 mm x up to 600 mm |
| (3) Heat transfer surface area | 248 m2/m3 | 152 m2/m3 | 120 m2/m3 |
| (4) Void | 97 % | 96 % | 96 % |
| (5) Cross corrugated flutes angle | 60 º | 60 º | 60 º |

Table 2 Dependence of the parameters βcch,da&βcch,ma on wet bulb temperature(ta,wb) and pad module thicknesses (δ) at constant dry bulb temperature (ta,db), air- velocity(Va.) , Pad module type: Onda 27

| Va.=1.33 m/s |  |  |  |  |  |  |  | Va.=2.67 m/s |  |  |  |  |  |  |  | ta,wb | ta,db |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| δ=0.4 m |  | δ=0.3 m |  | δ=0.2 m |  | δ=0.1 m |  | δ=0.4 m |  | δ=0.3 m |  | δ=0.2 m |  | δ=0.1 m |  |  |  |
| βcch,ma | βcch,da | βcch,ma | βcch,da | βcch,ma | βcch,da | βcch,ma | βcch,da | βcch,ma | βcch,da | βcch,ma | βcch,da | βcch,ma | βcch,da | βcch,ma | βcch,da |  |  |
| 2.805 | 2.795 | 2.903 | 2.893 | 3.048 | 3.037 | 3.312 | 3.301 | 2.805 | 2.795 | 2.903 | 2.893 | 3.048 | 3.037 | 3.312 | 3.301 | 17 | 43 |
| 2.828 |  | 2.928 |  | 3.074 |  | 3.340 |  | 2.828 |  | 2.928 |  | 3.074 |  | 3.340 |  | 19 |  |
| 2.852 |  | 2.953 |  | 3.100 |  | 3.369 |  | 2.852 |  | 2.953 |  | 3.100 |  | 3.369 |  | 21 |  |
| 2.883 |  | 2.984 |  | 3.133 |  | 3.404 |  | 2.883 |  | 2.984 |  | 3.133 |  | 3.404 |  | 23.5 |  |
| 2.907 |  | 3.009 |  | 3.159 |  | 3.433 |  | 2.907 |  | 3.009 |  | 3.159 |  | 3.433 |  | 25.5 |  |
| 2.806 | 2.765 | 2.905 | 2.862 | 3.050 | 3.005 | 3.314 | 3.266 | 2.806 | 2.765 | 2.905 | 2.862 | 3.050 | 3.005 | 3.314 | 3.266 | 17 | 35 |
| 2.828 |  | 2.927 |  | 3.073 |  | 3.340 |  | 2.828 |  | 2.927 |  | 3.073 |  | 3.340 |  | 19 |  |
| 2.850 |  | 2.950 |  | 3.097 |  | 3.366 |  | 2.850 |  | 2.950 |  | 3.097 |  | 3.366 |  | 21 |  |
| 2.878 |  | 2.979 |  | 3.127 |  | 3.398 |  | 2.878 |  | 2.979 |  | 3.127 |  | 3.398 |  | 23.5 |  |
| 2.900 |  | 3.002 |  | 3.151 |  | 3.425 |  | 2.900 |  | 3.002 |  | 3.151 |  | 3.425 |  | 25.5 |  |

Table 3 Dependence of the parameters βcch,da&βcch,ma on pad module type at different dry- and wet bulb temperatures (ta,db, ta,wb) and constant air- velocity(Va.) and pad module thicknesses (δ)

| ta,db | ta,wb | Onda12 |  | Onda19 |  | Onda27 |  | Onda12 |  | Onda19 |  | Onda27 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Va.= 2.67 m/s, δ=0.3m |  |  |  |  |  | Va. = 0.67 m/s, δ=0.3m |  |  |  |  |  |
|  |  | βcch,da | βcch,ma | βcch,da | βcch,ma | βcch,da | βcch,ma | βcch,da | βcch,ma | βcch,da | βcch,ma | βcch,da | βcch,ma |
| 43 | 17 | 6.336 | 6.381 | 3.734 | 3.748 | 2.893 | 2.903 | 6.121 | 6.164 | 3.608 | 3.621 | 2.795 | 2.805 |
|  | 19 |  | 6.432 |  | 3.779 |  | 2.928 |  | 6.214 |  | 3.651 |  | 2.828 |
|  | 21 |  | 6.485 |  | 3.811 |  | 2.953 |  | 6.265 |  | 3.682 |  | 2.852 |
|  | 23.5 |  | 6.551 |  | 3.852 |  | 2.984 |  | 6.329 |  | 3.721 |  | 2.883 |
|  | 25.5 |  | 6.604 |  | 3.884 |  | 3.009 |  | 6.380 |  | 3.752 |  | 2.907 |
| 35 | 17 | 6.269 | 6.377 | 3.695 | 3.750 | 2.862 | 2.905 | 6.057 | 6.160 | 3.570 | 3.623 | 2.765 | 2.806 |
|  | 19 |  | 6.424 |  | 3.779 |  | 2.927 |  | 6.206 |  | 3.650 |  | 2.828 |
|  | 21 |  | 6.472 |  | 3.808 |  | 2.950 |  | 6.252 |  | 3.679 |  | 2.850 |
|  | 23.5 |  | 6.533 |  | 3.845 |  | 2.979 |  | 6.311 |  | 3.714 |  | 2.878 |
|  | 25.5 |  | 6.581 |  | 3.875 |  | 3.002 |  | 6.358 |  | 3.743 |  | 2.900 |

Table 4 Dependence of the parameters Acch,da&Acch,ma on wet bulb temperatures (ta,wb)  at constant dry bulb temperature (ta,db), air- velocity(Va.) and different pad module thicknesses (δ) (Pad module type: Onda 12)

| ta,db | ta,wb | Va.=2.00 m/s |  |  |  |  |  |  |  | Va.=0.67 m/s |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | δ=0.1m |  | δ=0.2m |  | δ=0.3m |  | δ=0.4m |  | δ=0.1m |  | δ=0.2m |  | δ=0.3m |  | δ=0.4m |  |  |
|  |  | Acch,da | Acch,ma | Acch,da | Acch,ma | Acch,da | Acch,ma | Acch,da | Acch,ma | Acch,da | Acch,ma | Acch,da | Acch,ma | Acch,da | Acch,ma | Acch,da | Acch,ma |
| 43 | 17 | 32.620 | 33.041 | 30.016 | 30.404 | 28.591 | 28.960 | 27.621 | 27.978 | 32.620 | 33.041 | 30.016 | 30.404 | 28.591 | 28.960 | 27.621 | 27.978 |
|  | 19 |  | 33.409 |  | 30.743 |  | 29.283 |  | 28.289 |  | 33.409 |  | 30.743 |  | 29.283 |  | 28.289 |
|  | 21 |  | 33.791 |  | 31.094 |  | 29.617 |  | 28.612 |  | 33.791 |  | 31.094 |  | 29.617 |  | 28.612 |
|  | 23.5 |  | 34.286 |  | 31.550 |  | 30.051 |  | 29.032 |  | 34.286 |  | 31.550 |  | 30.051 |  | 29.032 |
|  | 25.5 |  | 34.698 |  | 31.929 |  | 30.413 |  | 29.381 |  | 34.698 |  | 31.929 |  | 30.413 |  | 29.381 |
| 35 | 17 | 33.102 | 33.989 | 30.460 | 31.277 | 29.013 | 29.791 | 28.029 | 28.780 | 33.102 | 33.989 | 30.460 | 31.277 | 29.013 | 29.791 | 28.029 | 28.780 |
|  | 19 |  | 34.344 |  | 31.603 |  | 30.102 |  | 29.080 |  | 34.344 |  | 31.603 |  | 30.102 |  | 29.080 |
|  | 21 |  | 34.711 |  | 31.941 |  | 30.424 |  | 29.392 |  | 34.711 |  | 31.941 |  | 30.424 |  | 29.392 |
|  | 23.5 |  | 35.190 |  | 32.382 |  | 30.844 |  | 29.797 |  | 35.190 |  | 32.382 |  | 30.844 |  | 29.797 |
|  | 25.5 |  | 35.589 |  | 32.748 |  | 31.193 |  | 30.135 |  | 35.589 |  | 32.748 |  | 31.193 |  | 30.135 |

Table 5 Dependence of the parameters βcdm,da&βcdm,ma on wet bulb temperatures (ta,wb) and pad module thicknesses (δ)  at constant dry bulb temperature (ta,db), air- velocity(Va.) , Pad module type: Onda 19

| Va.=0.67 m/s |  |  |  |  |  |  |  | Va.=2.00 m/s |  |  |  |  |  |  |  | ta,wb | ta,db |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| δ=0.4 m |  | δ=0.3 m |  | δ=0.2 m |  | δ=0.1 m |  | δ=0.4 m |  | δ=0.3 m |  | δ=0.2 m |  | δ=0.1 m |  |  |  |
| βcdm,ma | βcdm,da | βcdm,ma | βcdm,da | βcdm,ma | βcdm,da | βcdm,ma | βcdm,da | βcdm,ma | βcdm,da | βcdm,ma | βcdm,da | βcdm,ma | βcdm,da | βcdm,ma | βcdm,da |  |  |
| 3.134 | 3.134 | 3.244 | 3.244 | 3.406 | 3.406 | 3.701 | 3.701 | 3.134 | 3.134 | 3.244 | 3.244 | 3.406 | 3.406 | 3.701 | 3.701 | 17 | 43 |
| 3.135 |  | 3.245 |  | 3.407 |  | 3.702 |  | 3.135 |  | 3.245 |  | 3.407 |  | 3.702 |  | 19 |  |
| 3.135 |  | 3.245 |  | 3.407 |  | 3.703 |  | 3.135 |  | 3.245 |  | 3.407 |  | 3.703 |  | 21 |  |
| 3.136 |  | 3.246 |  | 3.408 |  | 3.704 |  | 3.136 |  | 3.246 |  | 3.408 |  | 3.704 |  | 23.5 |  |
| 3.137 |  | 3.247 |  | 3.409 |  | 3.705 |  | 3.137 |  | 3.247 |  | 3.409 |  | 3.705 |  | 25.5 |  |
| 3.101 | 3.100 | 3.210 | 3.209 | 3.370 | 3.369 | 3.662 | 3.661 | 3.101 | 3.100 | 3.210 | 3.209 | 3.370 | 3.369 | 3.662 | 3.661 | 17 | 35 |
| 3.102 |  | 3.211 |  | 3.371 |  | 3.663 |  | 3.102 |  | 3.211 |  | 3.371 |  | 3.663 |  | 19 |  |
| 3.102 |  | 3.211 |  | 3.371 |  | 3.664 |  | 3.102 |  | 3.211 |  | 3.371 |  | 3.664 |  | 21 |  |
| 3.103 |  | 3.212 |  | 3.372 |  | 3.665 |  | 3.103 |  | 3.212 |  | 3.372 |  | 3.665 |  | 23.5 |  |
| 3.104 |  | 3.213 |  | 3.373 |  | 3.666 |  | 3.104 |  | 3.213 |  | 3.373 |  | 3.666 |  | 25.5 |  |

Table 6 Dependence of the parameters βcdm,da&βcdm,ma on pad module type at different dry- and wet bulb temperatures (ta,db, ta,wb) and constant air- velocity(Va.) and pad module thicknesses (δ)

| ta,db | ta,wb | Onda12 |  | Onda19 |  | Onda27 |  | Onda12 |  | Onda19 |  | Onda27 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Va.= 2.00 m/s, δ=0.4m |  |  |  |  |  | Va. = 0.67 m/s, δ=0.4m |  |  |  |  |  |
|  |  | βcdm,da | βcdm,ma | βcdm,da | βcdm,ma | βcdm,da | βcdm,ma | βcdm,da | βcdm,ma | βcdm,da | βcdm,ma | βcdm,da | βcdm,ma |
| 43 | 17 | 5.317 | 5.318 | 3.134 | 3.134 | 2.428 | 2.428 | 5.3173 | 5.3181 | 3.134 | 3.134 | 2.428 | 2.428 |
|  | 19 |  | 5.319 |  | 3.135 |  | 2.428 |  | 5.3190 |  | 3.135 |  | 2.428 |
|  | 21 |  | 5.320 |  | 3.135 |  | 2.429 |  | 5.3201 |  | 3.135 |  | 2.429 |
|  | 23.5 |  | 5.321 |  | 3.136 |  | 2.429 |  | 5.3215 |  | 3.136 |  | 2.429 |
|  | 25.5 |  | 5.323 |  | 3.137 |  | 2.430 |  | 5.3227 |  | 3.137 |  | 2.430 |
| 35 | 17 | 5.260 | 5.262 | 3.100 | 3.101 | 2.402 | 2.402 | 5.2600 | 5.2620 | 3.100 | 3.101 | 2.402 | 2.402 |
|  | 19 |  | 5.263 |  | 3.102 |  | 2.403 |  | 5.2630 |  | 3.102 |  | 2.403 |
|  | 21 |  | 5.264 |  | 3.102 |  | 2.403 |  | 5.2641 |  | 3.102 |  | 2.403 |
|  | 23.5 |  | 5.266 |  | 3.103 |  | 2.404 |  | 5.2655 |  | 3.103 |  | 2.404 |
|  | 25.5 |  | 5.267 |  | 3.104 |  | 2.405 |  | 5.2668 |  | 3.104 |  | 2.405 |

Table 7 Dependence of the parameters Acdm,da&Acdm,ma on wet bulb temperatures (ta,wb)  at constant

dry bulb temperature (ta,db), air-velocity(Va.) and different pad module thicknesses (δ) (Pad module type: Onda 27)

| ta,db | ta,wb | Va.=2.67 m/s |  |  |  |  |  |  |  | Va.=0.67 m/s |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | δ=0.1m |  | δ=0.2m |  | δ=0.3m |  | δ=0.4m |  | δ=0.1m |  | δ=0.2m |  | δ=0.3m |  | δ=0.4m |  |
|  |  | Acdm,da | Acdm,ma | Acdm,da | Acdm,ma | Acdm,da | Acdm,ma | Acdm,da | Acdm,ma | Acdm,da | Acdm,,ma | Acdm,da | Acdm,ma | Acdm,da | Acdm,ma | Acdm,da | Acdm,ma |
| 43 | 17 | 0.024 | 0.024 | 0.022 | 0.022 | 0.021 | 0.021 | 0.020 | 0.020 | 0.024 | 0.024 | 0.022 | 0.022 | 0.021 | 0.021 | 0.020 | 0.020 |
|  | 19 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 23.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 25.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 35 | 17 | 0.024 | 0.024 | 0.022 | 0.022 | 0.021 | 0.021 | 0.020 | 0.020 | 0.024 | 0.024 | 0.022 | 0.022 | 0.021 | 0.021 | 0.020 | 0.020 |
|  | 19 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 23.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 25.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Table 8 Dependence of the heat- and mass- transfer coefficients (  hcch,ma,in,kcdm,ma,in) on frontal air linear velocity ( Va.) for different pad module types and thicknesses (Asp,δ) at different air wet bulb temperatures (ta,wb) and constant air dry bulb temperature (ta,db=40 °C)

| ta,wb | Onda 12, Asp=248 m2m3. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Va.=2.67 m/s |  |  |  |  |  |  |  | Va.=0.67 m/s |  |  |  |  |  |  |  |
|  | δ=0.1 m |  | δ=0.2 m |  | δ=0.3 m |  | δ=0.4 m |  | δ=0.1 m |  | δ=0.2 m |  | δ=0.3 m |  | δ=0.4 m |  |
|  | hcch,ma,in | kcdm,ma,in | hcch,ma,in | kcdm,ma,in | hcch,ma,in | kcdm,ma,in | hcch,ma,in | kcdm,ma,in | hcch,ma,in | kcdm,ma,in | hcch,ma,in | kcdm,ma,in | hcch,ma,in | kcdm,ma,in | hcch,ma,in | kcdm,ma,in |
| 17 | 73.163 | 0.055 | 67.324 | 0.051 | 64.126 | 0.048 | 61.950 | 0.047 | 24.135 | 0.018 | 22.208 | 0.017 | 21.154 | 0.016 | 20.436 | 0.015 |
| 19 | 73.957 | 0.055 | 68.055 | 0.051 | 64.823 | 0.048 | 62.623 | 0.047 | 24.397 | 0.018 | 22.450 | 0.017 | 21.384 | 0.016 | 20.658 | 0.015 |
| 21 | 74.781 | 0.055 | 68.813 | 0.051 | 65.545 | 0.048 | 63.321 | 0.047 | 24.669 | 0.018 | 22.700 | 0.017 | 21.622 | 0.016 | 20.888 | 0.015 |
| 23.5 | 75.853 | 0.055 | 69.799 | 0.051 | 66.484 | 0.048 | 64.228 | 0.047 | 25.022 | 0.018 | 23.025 | 0.017 | 21.932 | 0.016 | 21.187 | 0.015 |
| 25.5 | 76.744 | 0.055 | 70.619 | 0.051 | 67.265 | 0.048 | 64.983 | 0.047 | 25.316 | 0.018 | 23.296 | 0.017 | 22.189 | 0.016 | 21.436 | 0.015 |
| ta,wb | Onda 27, Asp=120 m2m3. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 17 | 68.758 | 0.052 | 63.270 | 0.048 | 60.265 | 0.046 | 58.220 | 0.044 | 22.682 | 0.017 | 20.871 | 0.016 | 19.880 | 0.015 | 19.205 | 0.015 |
| 19 | 69.527 | 0.052 | 63.978 | 0.048 | 60.940 | 0.046 | 58.872 | 0.044 | 22.936 | 0.017 | 21.105 | 0.016 | 20.103 | 0.015 | 19.421 | 0.015 |
| 21 | 70.326 | 0.052 | 64.713 | 0.048 | 61.640 | 0.046 | 59.548 | 0.044 | 23.199 | 0.017 | 21.347 | 0.016 | 20.333 | 0.015 | 19.644 | 0.015 |
| 23.5 | 71.364 | 0.052 | 65.668 | 0.048 | 62.550 | 0.046 | 60.427 | 0.044 | 23.541 | 0.017 | 21.663 | 0.016 | 20.634 | 0.015 | 19.934 | 0.015 |
| 25.5 | 72.228 | 0.052 | 66.463 | 0.048 | 63.307 | 0.046 | 61.158 | 0.044 | 23.826 | 0.017 | 21.925 | 0.016 | 20.883 | 0.015 | 20.175 | 0.015 |

Table 9 Dependence of heat- and mass transfer coefficients (hcch,ma,in , kcdm,ma,in) and DEC-efficiencies (εcch,ma,in,  εcdm,ma,in)

on pad module type (Asp) at different air dry- and wet  bulb temperatures (ta,db,ta,wb) and constant air velocity

(Va.=2.00 m/s) and pad module thicknesses (δ=0.3m)

| ta,db | ta,wb | Onda 12, Asp=248 m2m3 |  |  |  | Onda 19, Asp=152 m2m3 |  |  |  | Onda 27, Asp = 120 m2m3 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | hcch,ma,in | εcch,ma,in | kcdm,ma,in | εcdm,ma,in | hcch,ma,in | εcch,ma,in | kcdm,ma,in | εcdm,ma,in | hcch,ma,in | εcch,ma,in | kcdm,ma,in | εcdm,ma,in |
| 43 | 17 | 50.403 | 0.811 | 0.039 | 0.810 | 48.245 | 0.624 | 0.037 | 0.622 | 47.341 | 0.532 | 0.036 | 0.529 |
|  | 19 | 50.964 | 0.814 | 0.039 | 0.812 | 48.798 | 0.627 | 0.037 | 0.625 | 47.884 | 0.535 | 0.036 | 0.532 |
|  | 21 | 51.545 | 0.816 | 0.039 | 0.815 | 49.372 | 0.630 | 0.037 | 0.628 | 48.447 | 0.538 | 0.036 | 0.535 |
|  | 23.5 | 52.302 | 0.819 | 0.039 | 0.818 | 50.118 | 0.634 | 0.037 | 0.632 | 49.179 | 0.541 | 0.036 | 0.538 |
|  | 25.5 | 52.930 | 0.822 | 0.039 | 0.820 | 50.737 | 0.637 | 0.037 | 0.635 | 49.787 | 0.544 | 0.036 | 0.541 |
| 35 | 17 | 51.849 | 0.811 | 0.038 | 0.810 | 49.703 | 0.624 | 0.037 | 0.622 | 48.772 | 0.532 | 0.036 | 0.530 |
|  | 19 | 52.389 | 0.813 | 0.038 | 0.812 | 50.238 | 0.627 | 0.037 | 0.625 | 49.297 | 0.534 | 0.036 | 0.532 |
|  | 21 | 52.950 | 0.816 | 0.038 | 0.814 | 50.793 | 0.630 | 0.037 | 0.628 | 49.841 | 0.537 | 0.036 | 0.534 |
|  | 23.5 | 53.681 | 0.818 | 0.038 | 0.817 | 51.516 | 0.634 | 0.037 | 0.631 | 50.550 | 0.541 | 0.036 | 0.538 |
|  | 25.5 | 54.289 | 0.821 | 0.038 | 0.819 | 52.117 | 0.637 | 0.037 | 0.634 | 51.140 | 0.543 | 0.036 | 0.540 |

Table 10 Dependence of DEC-efficiencies (εcch,ma,in,  εcdm,ma,in) on pad module type (Asp) at different : (i)  frontal air velocity(Va.), (ii) wet  bulb temperatures (ta,wb) and pad module thicknesses (δ) at constant air dry bulb temperature (ta,db=43 °C)

| ta,wb | Onda 12, Asp=248 m2m3. |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Va.=2.67 m/s |  |  |  | Va.=0.67 m/s |  |  |  |
|  | δ=0.1 m |  | δ=0.4 m |  | δ=0.1 m |  | δ=0.4 m |  |
|  | εcch,ma,in | εcdm,ma,in | εcch,ma,in | εcdm,ma,in | εcch,ma,in | εcdm,ma,in | εcch,ma,in | εcdm,ma,in |
| 17 | 0.450 | 0.448 | 0.868 | 0.867 | 0.546 | 0.544 | 0.931 | 0.930 |
| 19 | 0.453 | 0.450 | 0.870 | 0.869 | 0.549 | 0.546 | 0.933 | 0.932 |
| 21 | 0.456 | 0.453 | 0.873 | 0.871 | 0.552 | 0.549 | 0.934 | 0.933 |
| 23.5 | 0.459 | 0.456 | 0.875 | 0.874 | 0.555 | 0.552 | 0.936 | 0.935 |
| 25.5 | 0.462 | 0.458 | 0.877 | 0.876 | 0.558 | 0.555 | 0.937 | 0.937 |
| ta,wb | Onda 27, Asp=120 m2m3. |  |  |  |  |  |  |  |
|  | εcch,ma,in | εcdm,ma,in | εcch,ma,in | εcdm,ma,in | εcch,ma,in | εcdm,ma,in | εcch,ma,in | εcdm,ma,in |
| 17 | 0.238 | 0.237 | 0.602 | 0.600 | 0.302 | 0.300 | 0.704 | 0.702 |
| 19 | 0.240 | 0.238 | 0.605 | 0.603 | 0.304 | 0.301 | 0.707 | 0.705 |
| 21 | 0.242 | 0.239 | 0.609 | 0.606 | 0.306 | 0.303 | 0.710 | 0.708 |
| 23.5 | 0.244 | 0.240 | 0.612 | 0.610 | 0.309 | 0.305 | 0.714 | 0.711 |
| 25.5 | 0.246 | 0.241 | 0.615 | 0.612 | 0.311 | 0.307 | 0.717 | 0.714 |

Table 11 The dimensionless Shaaban’s (NSb,da) – and Lewis (NLe,da) numbers independence of design- and operating parameters of DEC when dry air properties are considered

| Onda 12, Asp=248 m2m3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ta,wb | ta,db | Va.=2.00 m/s |  |  |  |  | Va.=0.67 m/s |  |  |  |  |  |  | ta,db | Va.=2.00 m/s |  |  |  | Va.=0.67 m/s |  |  |  |
|  |  | δ=0.2 m |  | δ=0.4 m |  |  | δ=0.2 m |  |  |  | δ=0.4 m |  |  |  | δ=0.2 m |  | δ=0.4 m |  | δ=0.2 m |  | δ=0.4 m |  |
|  |  | NSb,da | NLe,da | NSb,da |  | NLe,da | NSb,da |  | NLe,da |  | NSb,da |  | NLe,da |  | NSb,da | NLe,da | NSb,da | NLe,da | NSb,da | NLe,da | NSb,da | NLe,da |
| 17.0 | 43 | 1.303 | 0.884 | 1.303 |  | 0.884 | 1.303 |  | 0.884 |  | 1.303 |  | 0.884 | 35 | 1.302 | 0.884 | 1.302 | 0.884 | 1.302 | 0.884 | 1.302 | 0.884 |
| 19.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 21.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 23.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 25.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Onda 27, Asp=120 m2m3. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ta,wb | ta,db | Va.=2.00 m/s |  |  |  |  |  | Va.=0.67 m/s |  |  |  |  |  | ta,db | Va.=2.00 m/s |  |  |  | Va.=0.67 m/s |  |  |  |
|  |  | δ=0.2 m |  | δ=0.4 m |  |  |  | δ=0.2 m |  |  |  | δ=0.4 m |  |  | δ=0.2 m |  | δ=0.4 m |  | δ=0.2 m |  | δ=0.4 m |  |
|  |  | NSb,da | NLe,da | NSb,da | NLe,da |  |  | NSb,da |  | NLe,da |  | NSb,da | NLe,da |  | NSb,da | NLe,da | NSb,da | NLe,da | NSb,da | NLe,da | NSb,da | NLe,da |
| 17.0 | 43 | 1.303 | 0.884 | 1.303 | 0.884 |  |  | 1.303 |  | 0.884 |  | 1.303 | 0.884 | 35 | 1.302 | 0.884 | 1.302 | 0.884 | 1.302 | 0.884 | 1.302 | 0.884 |
| 19.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 21.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 23.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 25.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Table 12 Effect of design- and operating parameters variations on the dimensionless Shaaban’s (Sbma)- and Lewis (NLe,ma) numbers  when humidified air properties are considered

| Onda 12, Asp=248 m2m3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ta,wb | ta,db | Va.=2.67 m/s |  |  |  | Va.=0.67 m/s |  |  |  |  |  |  | ta,db | Va.=2.67 m/s |  |  |  | Va.=0.67 m/s |  |  |  |
|  |  | δ=0.1 m |  | δ=0.4 m |  | δ=0.1 m |  |  | δ=0.4 m |  |  |  |  | δ=0.1 m |  | δ=0.4 m |  | δ=0.1 m |  | δ=0.4 m |  |
|  |  | NSb,ma | NLe,ma | NSb,ma | NLe,ma | NSb,ma | NLe,ma |  | NSb,ma |  | NLe,ma |  |  | NSb,ma | NLe,ma | NSb,ma | NLe,ma | NSb,ma | NLe,ma | NSb,ma | NLe,ma |
| 17 | 43 | 1.298 | 0.893 | 1.298 | 0.893 | 1.298 | 0.893 |  | 1.298 |  | 0.893 |  | 35 | 1.292 | 0.906 | 1.292 | 0.906 | 1.292 | 0.906 | 1.292 | 0.906 |
| 19 |  | 1.293 | 0.904 | 1.293 | 0.904 | 1.293 | 0.904 |  | 1.293 |  | 0.904 |  |  | 1.287 | 0.916 | 1.287 | 0.916 | 1.287 | 0.916 | 1.287 | 0.916 |
| 21 |  | 1.288 | 0.914 | 1.288 | 0.914 | 1.288 | 0.914 |  | 1.288 |  | 0.914 |  |  | 1.282 | 0.926 | 1.282 | 0.926 | 1.282 | 0.926 | 1.282 | 0.926 |
| 23.5 |  | 1.282 | 0.928 | 1.282 | 0.928 | 1.282 | 0.928 |  | 1.282 |  | 0.928 |  |  | 1.277 | 0.939 | 1.277 | 0.939 | 1.277 | 0.939 | 1.277 | 0.939 |
| 25.5 |  | 1.276 | 0.939 | 1.276 | 0.939 | 1.276 | 0.939 |  | 1.276 |  | 0.939 |  |  | 1.272 | 0.949 | 1.272 | 0.949 | 1.272 | 0.949 | 1.272 | 0.949 |
| Onda 27, Asp=120 m2m3. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ta,wb | ta,db | Va.=2.67 m/s |  |  |  | Va.=0.67 m/s |  |  |  |  |  |  | ta,db | Va.=2.67 m/s |  |  |  | Va.=0.67 m/s |  |  |  |
|  |  | δ=0.1 m |  | δ=0.4 m |  | δ=0.1 m |  |  |  | δ=0.4 m |  |  |  | δ=0.1 m |  | δ=0.4 m |  | δ=0.1 m |  | δ=0.4 m |  |
|  |  | NSb,ma | NLe,ma | NSb,ma | NLe,ma | NSb,ma |  | NLe,ma |  | NSb,ma |  | NLe,ma |  | NSb,ma | NLe,ma | NSb,ma | NLe,ma | NSb,ma | NLe,ma | NSb,ma | NLe,ma |
| 17 | 43 | 1.300 | 0.888 | 1.300 | 0.888 | 1.300 |  | 0.888 |  | 1.300 |  | 0.888 | 35 | 1.293 | 0.903 | 1.293 | 0.903 | 1.293 | 0.903 | 1.293 | 0.903 |
| 19 |  | 1.295 | 0.899 | 1.295 | 0.899 | 1.295 |  | 0.899 |  | 1.295 |  | 0.899 |  | 1.288 | 0.914 | 1.288 | 0.914 | 1.288 | 0.914 | 1.288 | 0.914 |
| 21 |  | 1.290 | 0.911 | 1.290 | 0.911 | 1.290 |  | 0.911 |  | 1.290 |  | 0.911 |  | 1.283 | 0.924 | 1.283 | 0.924 | 1.283 | 0.924 | 1.283 | 0.924 |
| 23.5 |  | 1.283 | 0.925 | 1.283 | 0.925 | 1.283 |  | 0.925 |  | 1.283 |  | 0.925 |  | 1.277 | 0.937 | 1.277 | 0.937 | 1.277 | 0.937 | 1.277 | 0.937 |
| 25.5 |  | 1.278 | 0.936 | 1.278 | 0.936 | 1.278 |  | 0.936 |  | 1.278 |  | 0.936 |  | 1.273 | 0.948 | 1.273 | 0.948 | 1.273 | 0.948 | 1.273 | 0.948 |

Table 13 % Uncertainties of DEC-efficiency (εcch) and heat transfer coefficient (∆hcch/hcch)

| ta,db | ta,wb | Onda 12, Asp=248 m2m3. |  | Onda 19, Asp=152 m2m3. |  | Onda 27, Asp=120 m2m3. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Va.=2.67 ms ; δ=0.2 m |  | Va.=0.67 ms ; δ=0.4 m |  | Va.=2.67 ms ; δ=0.2 m |  |
|  |  | (εcch) %uncertainty | (∆hcchh)cch %uncertainty | (εcch) %uncertainty | (∆hcchh)cch %uncertainty | (εcch) %uncertainty | (∆hcchh)cch %uncertainty |
| 43 | 17.0 | 7.7677 | 14.1359 | 7.0961 | 17.2305 | 15.4569 | 11.9595 |
|  | 19.0 | 13.9378 | 25.5534 | 9.0524 | 22.2199 | 16.2923 | 12.5927 |
|  | 21.0 | 13.4078 | 24.7247 | 10.5023 | 26.0581 | 17.5758 | 13.5706 |
|  | 23.5 | 11.0073 | 20.4443 | 9.1590 | 23.0328 | 20.0993 | 15.4999 |
|  | 25.5 | 12.0148 | 22.4591 | 9.0243 | 22.9526 | 21.0161 | 16.1958 |
| 35 | 17.0 | 10.1096 | 18.4167 | 8.9589 | 21.8293 | 19.5677 | 15.1553 |
|  | 19.0 | 11.9148 | 21.8291 | 9.8869 | 24.3256 | 21.4018 | 16.5615 |
|  | 21.0 | 13.6094 | 25.0756 | 9.0899 | 22.5834 | 23.5569 | 18.2150 |
|  | 23.5 | 12.4183 | 23.0383 | 9.8638 | 24.8263 | 25.5387 | 19.7325 |
|  | 25.5 | 13.6223 | 25.4223 | 12.0080 | 30.5550 | 26.8223 | 20.7149 |

| ta,db | ta,wb | Onda 12, Asp=248 m2m3. |  | Onda 19, Asp=152 m2m3. |  | Onda 27, Asp=120 m2m3. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Va.=2.00 ms ; δ=0.3 m |  | Va.=1.33 ms ; δ=0.3 m |  | Va.=1.33 ms ; δ=0.3 m |  |
|  |  | (εcdm) %uncertainty | ∆kcdmkcdm %uncertainty | (εcdm) %uncertainty | (∆kcdmk)cdm %uncertainty | (εcdm) %uncertainty | (∆kcdmk)cdm %uncertainty |
| 43 | 17 | 2.2262 | 4.6778 | 1.9891 | 2.5531 | 1.9275 | 1.8888 |
|  | 19 | 2.8534 | 6.3320 | 3.0714 | 4.9108 | 2.8604 | 3.9112 |
|  | 21 | 3.7060 | 8.4996 | 4.6063 | 7.8958 | 4.2297 | 6.4086 |
|  | 23.5 | 3.9085 | 9.0391 | 4.8879 | 8.4737 | 4.7918 | 7.4311 |
|  | 25.5 | 9.2589 | 22.1176 | 9.4286 | 16.9118 | 8.2952 | 13.3946 |
| 35 | 17 | 3.0876 | 6.8657 | 3.2576 | 5.2601 | 3.3204 | 4.7528 |
|  | 19 | 4.6949 | 10.8429 | 5.2800 | 9.1201 | 4.7637 | 7.3092 |
|  | 21 | 8.2788 | 19.5052 | 8.4395 | 14.9560 | 38.1509 | 61.9911 |
|  | 23.5 | 8.9901 | 21.2831 | 11.0296 | 19.7542 | 9.3040 | 15.0237 |
|  | 25.5 | 12.3343 | 29.3731 | 11.0193 | 19.8141 | 11.8978 | 19.4313 |

Table 14 % Uncertainties of DEC-efficiencies (εcdm)  and mass transfer coefficient∆kcdmkcdm